## Rules
New Rule ID | Old Rule ID | Ruleset Reference | Rule Description | Applicable RMR | Rule Assertion | Comparison Value | Primary Rule | Notes | RDS | Evaluated? | General- P RMR = U RMR | General- P RMR = B RMR | Move to General?
21-1 | 21-1 | G3.1.1.3 | For systems using purchased hot water or steam, the heating source shall be modeled as purchased hot water or steam in both the proposed design and baseline building design. If any system in the proposed design uses purchased hot water or steam, all baseline systems with hot water coils shall use the same type of purchased hot water or steam. | Baseline RMR | = | Proposed RMR | No |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-1.md | Y | N | N | N
21-2 | 21-2 | G3.1.3.5 | For purchased HW/steam in the proposed model, the baseline shall have the same number of pumps as proposed | Baseline RMR | = | Proposed RMR | No |  | No RDS | Y | N | N | N
21-3 | 21-3 | G3.1.2.2 | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | Baseline RMR | = | Expected Value | Yes |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-3.md | Y | N | N | N
21-4 | 21-4 | G3.1.3.2 | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | Baseline RMR | = | Expected Value | Yes | Note: this has an RDS but was marked as secondary | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-4.md | Y | N | N | N
21-5 | 21-5 | G3.1.3.2 | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | Baseline RMR | = | Expected Value | Yes | Baseline number of HW Loops > 0 and number of boilers in HW loop >1 | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-5.md | Y | N | N | N
21-6 | 21-6 | G3.1.3.2 | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | Baseline RMR | = | Expected Value | Yes | Number of boilers -= 2 | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-6.md | Y | N | N | N
21-7 | 21-7 | G3.1.3.3 | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | Baseline RMR | = | Expected Value | Yes |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-7.md | Y | N | N | N
21-8 | 21-8 | G3.1.3.4 | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12),, HWST for the baseline building shall be reset using an outdoor air dry-bulb reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | Baseline RMR | = | Expected Value | Yes |  | No RDS | Y | N | N | N
21-9 | 21-9 | G3.1.3.5 | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | Baseline RMR | = | Expected Value | Yes | Excludes P HW/Steam. | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-9.md | Y | N | N | N
21-10 | 21-10 | G3.1.3.5 | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | Baseline RMR | = | Expected Value | Yes |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-10.md | Y | N | N | N
21-11 | 21-11A | G3.1.3.5 | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | Baseline RMR | = | Expected Value | Yes |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-11.md | Y | N | N | N
21-12 | 21-11B | G3.1.3.5 | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | Baseline RMR | = | Expected Value | Yes |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-12.md | Y | N | N | N
21-13 | 21-11C | G3.1.3.5 | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | Baseline RMR | = | Expected Value | Yes |  | https://github.com/pnnl/ruleset-checking-tool/blob/develop/docs/section21/Rule21-13.md | Y | N | N | N
21-14 | 21-14 | G3.1.3.4 | When the baseline building is modeled with a hot water plant, served by purchased HW system, hot water supply temperature reset is not modeled. | Baseline RMR | = | Expected Value | No |  | Need RDS to determine applicability | Y | N | N | N
21-15 | 21-15 | G3.1.3.5 | When the baseline building is modeled with a hot water plant, served by purchased HW system, the hot water pump power shall be 14 W/gpm | Baseline RMR | = | Expected Value | No |  | Need RDS to determine applicability | Y | N | N | N
21-16 | 21-18 | G3.1.3.2 | Baseline shall have only one heating hot water plant. | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N
21-17 | 21-19 | G3.1.2.1 | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N
21-18 | 21-21 | G3.1.2.1 | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | Baseline RMR | = | Expected Value | Yes |  |  | Y | N | N | N

## Sheet1
1 | Why are 21-18, 21-19, 21-20, and 21-21 missing?
2 | Why are tests for non-mandatory rules 21-4 and 21-8 being included?
3 | Why are 21-4 and 21-8 not mandatory?
4 | I don’t think the rule for 21-17 is correct, there is not an exception for purchased heating to be modeled only with primary only for systems serving more than 120,000 ft2
5 | Why no rule for G3.1.3.6 piping losses?
6 | 21-4 a, b – the requirement “Boilers should be modeled if baseline system = 1,5,7,11,12” is part of what should be tested and does not seem to be tested in TCD. Maybe it is tested somewhere else. The part about natural draft works fine. From RDS it implies that the first part is ok since it includes a boiler. Not sure if it is part of the predicate, then it should be tested otherwise it should not be part of the predicate
7 | the 21-5c test is almost identical to 21-5a and does not really test anything new that I could tell and could be deleted
8 | for 21-5, another test case should be added that is over 15,000 sqft and has one boiler that should fail.
9 | for 21-6a the operation upper limit for “Boiler 1” should be 70000 not 35000 otherwise both boilers would not be on for loads above 35000.
10 | for 21-7 a, b, the tests do not cover when just the supply temperature is not 180 but the return is 130. This test case should be added.
11 | for 21-7 a, b, the tests do not cover the return is not 130 but the supply is 180. This test case should be added.
12 | for 21-8 a, b, c, the wrong data elements are being referenced in FluidLoopDesignAndControl they should be: loop_supply_temperature_at_outdoor_high and loop_supply_temperature_at_outdoor_low. The data element design_return_temperature should not getting referenced at all.
13 | for 21-8 a, b, c, additional failing test cases should be added for each number in the reset strategy that is not matched. Currently only one of the temperatures is being tested, 21-8b. Three additional test cases that fail should be added for the other three temperatures.
14 | for 21-9 a, b, c, pump specification_method should be set to SIMPLE for 21-9a, 21-9c and to DETAILED for 21-9b.
15 | for 21-9 a, b, c, another unit test that uses Pump specification_method set to DETAILED that fails should be added.
16 | for 21-10 a, b, c, tests 21-10a and 21-10b are supposed to have 12,000 sqft but the zones add up to 100,000 sqft
17 | for 21-10 a, b, c, tests 21-10c and 21-10d are supposed to have 150,000 sqft but the zones add up to 100,000 sqft
18 | for 21-10 a, b, c, test 21-10b, I believe is supposed to be Pump speed_control set to VARIABLE_SPEED to fail as expected.
19 | missing unit tests for 21-11A, 21-11B, 21-11C, these are mandatory

## RuleCategorization
Rule Catergorization | Catergorization Base don Relvant System Impacted
Input Rules​: Transformation rules ​
Input Rules​: Minimum efficiency (backstop) rules
Input Rules: QC rules ​
Output Rules: Performance metric calculation rules ​
Output Rules: Reporting rules ​
Output Rules: QC Rules
General: Software requirement rules
General: Compliance Verification

## Templates
| lookup | key1 | key2 | key3 | key4 | data_group | object_id | parent_id | data_element | unit_type | units | System_7_VAV_HW_Reheat | PurchasedWater | Boiler | rule-21-1-a | rule-21-1-b | rule-21-2-a | rule-21-2-b | System_1_PTAC | System_1a_PTAC | System_1b_PTAC | System_1c_PTAC | System_2_PTHP | System_3_PSZ_AC_Gas_Furnace | System_3a_PSZ_AC_Gas_Furnace | System_3b_PSZ_AC_Gas_Furnace | System_3c_PSZ_AC_Gas_Furnace | System_4_PSZ_HP | System_5_PVAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_6_PVAV_Elec_Reheat | System_6b_PVAV_Elec_Reheat | System_7_VAV_HW_Reheat | System_7a_VAV_HW_Reheat | System_7b_VAV_HW_Reheat | System_7c_VAV_HW_Reheat | System_8_PFP_Reheat | System_8a_PFP_Reheat | System_8b_PFP_Reheat | System_8c_PFP_Reheat | System_9_Warm_Air_Furnace_Gas | System_9b_Warm_Air_Furnace_Gas | System_10_Warm_Air_Furnace_Elec | System_11.1_VAV_SZ | System_11.1a_VAV_SZ | System_11.1b_VAV_SZ | System_11.1c_VAV_SZ | System_11.2_VAV_SZ | System_11.2a_VAV_SZ | System 12_CAV_SZ_HW | System 12a_CAV_SZ_HW | System 12b_CAV_SZ_HW | System 13_CAV_SZ_ER | System 13_CAV_SZ_ER | Sys_1a_KJW
id::: | id::: | id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
weather:climate_zone:: | weather:climate_zone:: | weather | climate_zone |  |  | Calendar | N/A | ASHRAE229 1 | is_leap_year
ruleset_model_instances[0]:id:: | ruleset_model_instances[0]:id:: | ruleset_model_instances[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
JSON_PATH:buildings[0]:id:: | JSON_PATH:buildings[0]:id:: | JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
JSON_PATH:buildings[0]:building_open_schedule:: | JSON_PATH:buildings[0]:building_open_schedule:: | JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
JSON_PATH: building_segments[0]:id:: | JSON_PATH: building_segments[0]:id:: | JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
JSON_PATH:zones[0]:id:: | JSON_PATH:zones[0]:id:: | JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
JSON_PATH:zones[0]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[0]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[0]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[0]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[0]:spaces[0]:id: | JSON_PATH:zones[0]:spaces[0]:id: | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
JSON_PATH:zones[0]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[0]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
JSON_PATH:zones[0]:spaces[0]:floor_area: | JSON_PATH:zones[0]:spaces[0]:floor_area: | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
JSON_PATH:zones[0]:terminals[0]:id: | JSON_PATH:zones[0]:terminals[0]:id: | JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | VAV Air Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTHP Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | PTAC Terminal 1a
JSON_PATH:zones[0]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[0]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | false | false | false | false | false | false | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | FALSE
JSON_PATH:zones[0]:terminals[0]:heating_source: | JSON_PATH:zones[0]:terminals[0]:heating_source: | JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: ELECTRIC; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; FALSE: HOT_WATER
JSON_PATH:zones[0]:terminals[0]:heating_from_loop: | JSON_PATH:zones[0]:terminals[0]:heating_from_loop: | JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; FALSE: Boiler Loop 1
JSON_PATH:zones[0]:terminals[0]:type: | JSON_PATH:zones[0]:terminals[0]:type: | JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | VARIABLE_AIR_VOLUME | [6 empty] | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME
JSON_PATH:zones[0]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[0]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTHP 1 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 4 | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | System 9 | System 9B | System 10 | System 11 | System 11 | System 11 | System 11 | System 11 | System 11 | System 12 | System 12 | System 12 | System 13 | System 13 | PTAC 1a
#N/A | JSON_PATH:zones[0]:terminals[0]:cooling_source: | JSON_PATH:zones[0] | terminals[0] | cooling_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | FALSE: CHILLED_WATER
#N/A | JSON_PATH:zones[0]:terminals[0]:cooling_from_loop: | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | FALSE: Purchased CHW Loop 1
#N/A | JSON_PATH:zones[0]:terminals[0]:fan:id | JSON_PATH:zones[0] | terminals[0] | fan | id | Fan | Fan 1 | Terminal 1 | id |  |  | FALSE: Fan 1a
JSON_PATH:zones[0]:terminals[0]:fan_configuration: | JSON_PATH:zones[0]:terminals[0]:fan_configuration: | JSON_PATH:zones[0] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 1 | Zone 1 | fan_configuration |  |  | TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL
JSON_PATH:zones[1]:id:: | JSON_PATH:zones[1]:id:: | JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id |  |  | true: Thermal Zone 2; false: Thermal Zone 2; false: Thermal Zone 2; false: Thermal Zone 2; false: Thermal Zone 2; false: Thermal Zone 2; false: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2
JSON_PATH:zones[1]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[1]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | true: Required Cooling Schedule 1; false: Required Cooling Schedule 1; false: Required Cooling Schedule 1; false: Required Cooling Schedule 1; false: Required Cooling Schedule 1; false: Required Cooling Schedule 1; false: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1
JSON_PATH:zones[1]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[1]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | true: Required Heating Schedule 1; false: Required Heating Schedule 1; false: Required Heating Schedule 1; false: Required Heating Schedule 1; false: Required Heating Schedule 1; false: Required Heating Schedule 1; false: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1
JSON_PATH:zones[1]:spaces[0]:id: | JSON_PATH:zones[1]:spaces[0]:id: | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
JSON_PATH:zones[1]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[1]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
JSON_PATH:zones[1]:spaces[0]:floor_area: | JSON_PATH:zones[1]:spaces[0]:floor_area: | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
JSON_PATH:zones[1]:terminals[0]:id: | JSON_PATH:zones[1]:terminals[0]:id: | JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id |  |  | true: VAV Air Terminal 2; false: Terminal 2; false: Terminal 2; false: Terminal 2; false: Terminal 2; false: Terminal 2; false: Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2
JSON_PATH:zones[1]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[1]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | true: true; false: false; false: false; false: false; false: false; false: false; false: false; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE
JSON_PATH:zones[1]:terminals[0]:heating_source: | JSON_PATH:zones[1]:terminals[0]:heating_source: | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: ELECTRIC; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER
JSON_PATH:zones[1]:terminals[0]:type: | JSON_PATH:zones[1]:terminals[0]:type: | JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type |  |  | true: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME
JSON_PATH:zones[1]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[1]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_system |  |  | true: System 7; false: AHU_HW_System1; false: AHU_HW_System1; false: AHU_HW_System1; false: AHU_HW_System1; false: AHU_HW_System1; false: AHU_HW_System1; TRUE: System 5; TRUE: System 5; TRUE: System 6; TRUE: System 6; TRUE: System 7; TRUE: System 7; TRUE: System 7; TRUE: System 7; TRUE: System 8; TRUE: System 8; TRUE: System 8; TRUE: System 8
JSON_PATH:zones[1]:terminals[0]:heating_source: | JSON_PATH:zones[1]:terminals[0]:heating_source: | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: ELECTRIC; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER
JSON_PATH:zones[1]:terminals[0]:heating_from_loop: | JSON_PATH:zones[1]:terminals[0]:heating_from_loop: | JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  | true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1
JSON_PATH:zones[1]:terminals[0]:fan:id | JSON_PATH:zones[1]:terminals[0]:fan:id | JSON_PATH:zones[1] | terminals[0] | fan | id | Fan | Fan 2 | Terminal 2 | id
JSON_PATH:zones[1]:terminals[0]:fan_configuration: | JSON_PATH:zones[1]:terminals[0]:fan_configuration: | JSON_PATH:zones[1] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL; TRUE: PARALLEL
JSON_PATH:heating_ventilating_air_conditioning_systems[0]:id:: | JSON_PATH:heating_ventilating_air_conditioning_systems[0]:id:: | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System 7 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTHP 1 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 4 | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | System 9 | System 9B | System 10 | System 11 | System 11 | System 11 | System 11 | System 11 | System 11 | System 12 | System 12 | System 12 | System 13 | System 13 | PTAC 1a
JSON_PATH:heating_system:id:: | JSON_PATH:heating_system:id:: | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  |  | HHW Coil 1 | HHW Coil 1 | Heating System 1 | Heating System 1 | Heating System 1 | Heating System 1 | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | HP Heating Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | HP Coil 1 | [12 empty] | Furnace Coil 1 |  | Furnace Coil 1 | Heating Coil 1 | Heating Coil 1 | HHW Coil 1 | HHW Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Boiler Coil 1 | HHW Coil 1 | Heating Coil 1 | Heating Coil 1
JSON_PATH:heating_system:heating_system_type:: | JSON_PATH:heating_system:heating_system_type:: | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | HEAT_PUMP | FURNACE | FURNACE | FLUID_LOOP | FLUID_LOOP | HEAT_PUMP | [12 empty] | FURNACE |  | FURNACE | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE
JSON_PATH:heating_system:energy_source_type:: | JSON_PATH:heating_system:energy_source_type:: | JSON_PATH:heating_system | energy_source_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type |  |  | TRUE: NATURAL_GAS; TRUE: ELECTRICITY
JSON_PATH:heating_system:hot_water_loop:: | JSON_PATH:heating_system:hot_water_loop:: | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop |  |  | false: Purchased HW Loop 1; false: Boiler Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Purchased HW Loop 1; FALSE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1
JSON_PATH:preheat_system:id:: | JSON_PATH:preheat_system:id:: | JSON_PATH:preheat_system | id |  |  | HeatingSystem | Heating System 2 | HVAC 1 | id |  |  | true: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1
JSON_PATH:preheat_system:heating_system_type:: | JSON_PATH:preheat_system:heating_system_type:: | JSON_PATH:preheat_system | heating_system_type |  |  | HeatingSystem | Heating System 2 | HVAC 1 | heating_system_type |  |  | true: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: ELECTRIC_RESISTANCE; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: ELECTRIC_RESISTANCE; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP
JSON_PATH:preheat_system:hot_water_loop:: | JSON_PATH:preheat_system:hot_water_loop:: | JSON_PATH:preheat_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1
JSON_PATH:fan_system:id:: | JSON_PATH:fan_system:id:: | JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1 | [6 empty] | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 |  |  | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1
JSON_PATH:fan_system:fan_control:: | JSON_PATH:fan_system:fan_control:: | JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE | [6 empty] | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT |  |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT
JSON_PATH:fan_system:supply_fans[0]:id: | JSON_PATH:fan_system:supply_fans[0]:id: | JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | [6 empty] | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
JSON_PATH:fan_system:return_fans[0]:id: | JSON_PATH:fan_system:return_fans[0]:id: | JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 | [11 empty] | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
JSON_PATH:boilers[0]:id:: | JSON_PATH:boilers[0]:id:: | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | true: Boiler 1; false: Boiler 1; FALSE: Boiler 1; FALSE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; TRUE: Boiler 1; FALSE: Boiler 1
JSON_PATH:boilers[0]:loop:: | JSON_PATH:boilers[0]:loop:: | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | true: Boiler Loop 1; false: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; FALSE: Boiler Loop 1
#N/A | JSON_PATH:boilers[0]:draft_type:: | JSON_PATH:boilers[0] | draft_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type |  |  | false: NATURAL
#N/A | JSON_PATH:boilers[0]:rated_capacity:: | JSON_PATH:boilers[0] | rated_capacity |  |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr | false: 400000
#N/A | JSON_PATH:boilers[0]:efficiency:: | JSON_PATH:boilers[0] | efficiency |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency
#N/A | JSON_PATH:boilers[0]:efficiency_metric:: | JSON_PATH:boilers[0] | efficiency_metric |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric
JSON_PATH:boilers[0]:energy_source_type:: | JSON_PATH:boilers[0]:energy_source_type:: | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | true: NATURAL_GAS; FALSE: NATURAL_GAS; FALSE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; TRUE: NATURAL_GAS; FALSE: NATURAL_GAS
#N/A | JSON_PATH:boilers[0]:operation_lower_limit:: | JSON_PATH:boilers[0] | operation_lower_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit
#N/A | JSON_PATH:boilers[0]:operation_upper_limit:: | JSON_PATH:boilers[0] | operation_upper_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit
#N/A | JSON_PATH:boilers[1]:id:: | JSON_PATH:boilers[1] | id |  |  | Boiler | Boiler 2 | ASHRAE229 1 | id
#N/A | JSON_PATH:boilers[1]:loop:: | JSON_PATH:boilers[1] | loop |  |  | Boiler | Boiler 2 | ASHRAE229 1 | loop
#N/A | JSON_PATH:boilers[1]:draft_type:: | JSON_PATH:boilers[1] | draft_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
#N/A | JSON_PATH:boilers[1]:design_capacity:: | JSON_PATH:boilers[1] | design_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
#N/A | JSON_PATH:boilers[1]:energy_source_type:: | JSON_PATH:boilers[1] | energy_source_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
#N/A | JSON_PATH:boilers[1]:operation_lower_limit:: | JSON_PATH:boilers[1] | operation_lower_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit
#N/A | JSON_PATH:boilers[1]:operation_upper_limit:: | JSON_PATH:boilers[1] | operation_upper_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit
#N/A | JSON_PATH:boilers[2]:id:: | JSON_PATH:boilers[2] | id |  |  | Boiler | Boiler 3 | ASHRAE229 1 | id
#N/A | JSON_PATH:boilers[2]:loop:: | JSON_PATH:boilers[2] | loop |  |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
#N/A | JSON_PATH:boilers[2]:design_capacity:: | JSON_PATH:boilers[2] | design_capacity |  |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
JSON_PATH:chillers[0]:id:: | JSON_PATH:chillers[0]:id:: | JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | true: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1
JSON_PATH:chillers[0]:cooling_loop:: | JSON_PATH:chillers[0]:cooling_loop:: | JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | true: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1
JSON_PATH:chillers[0]:design_capacity:: | JSON_PATH:chillers[0]:design_capacity:: | JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[0]:energy_source_type:: | JSON_PATH:chillers[0]:energy_source_type:: | JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
JSON_PATH:chillers[0]:full_load_efficiency:: | JSON_PATH:chillers[0]:full_load_efficiency:: | JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
JSON_PATH:chillers[0]:compressor_type:: | JSON_PATH:chillers[0]:compressor_type:: | JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
JSON_PATH:chillers[1]:id:: | JSON_PATH:chillers[1]:id:: | JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id
JSON_PATH:chillers[1]:cooling_loop:: | JSON_PATH:chillers[1]:cooling_loop:: | JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[1]:design_capacity:: | JSON_PATH:chillers[1]:design_capacity:: | JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[2]:id:: | JSON_PATH:chillers[2]:id:: | JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id
JSON_PATH:chillers[2]:cooling_loop:: | JSON_PATH:chillers[2]:cooling_loop:: | JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[2]:design_capacity:: | JSON_PATH:chillers[2]:design_capacity:: | JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[3]:id:: | JSON_PATH:chillers[3]:id:: | JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id
JSON_PATH:chillers[3]:cooling_loop:: | JSON_PATH:chillers[3]:cooling_loop:: | JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[3]:design_capacity:: | JSON_PATH:chillers[3]:design_capacity:: | JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:cooling_system:id:: | JSON_PATH:cooling_system:id:: | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | CHW Coil 1 | [6 empty] | DX Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1 | HP Cooling Coil 1 | DX Coil 1 | Cooling Coil 1 | DX Coil 1 | Cooling Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 |  |  |  | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1
JSON_PATH:cooling_system:cooling_system_type:: | JSON_PATH:cooling_system:cooling_system_type:: | JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | FLUID_LOOP | [6 empty] | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
JSON_PATH:cooling_system:chilled_water_loop:: | JSON_PATH:cooling_system:chilled_water_loop:: | JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  | true: Secondary CHW Loop 1; FALSE: Purchased CHW 1; FALSE: Purchased CHW 1; TRUE: Purchased CHW Loop 1; TRUE: Purchased CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chiller Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1
JSON_PATH:external_fluid_source[0]:id:: | JSON_PATH:external_fluid_source[0]:id:: | JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  | false: Purchased HW 1; false: Purchased HW 1; false: Purchased HW 1; false: Purchased HW 1; FALSE: Purchased CHW 1; FALSE: Purchased HW 1; FALSE: Purchased HW 1; TRUE: Purchased CHW; TRUE: Purchased HW; TRUE: Purchased CHW; TRUE: Purchased HW 1; TRUE: Purchased HW 1; TRUE: Purchased CW 1; TRUE: Purchased HW 1; TRUE: Purchased HW 1; TRUE: Purchased CW 1; TRUE: Purchased HW 1; TRUE: Purchased HW 1; TRUE: Purchased HW 1; TRUE: Purchased CW 1; TRUE: Purchased HW 1; TRUE: Purchased HW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; TRUE: Purchased HW 1; FALSE: Purchased CHW
JSON_PATH:external_fluid_source[0]:loop:: | JSON_PATH:external_fluid_source[0]:loop:: | JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  | false: Purchased HW Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; FALSE: Purchased CHW Loop 1; FALSE: Purchased HW Loop 1; FALSE: Purchased HW Loop 1; TRUE: Purchased CHW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased CHW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; TRUE: Purchased HW Loop 1; FALSE: Purchased CHW Loop 1
JSON_PATH:external_fluid_source[0]:type:: | JSON_PATH:external_fluid_source[0]:type:: | JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  | false: HOT_WATER; false: HOT_WATER; false: HOT_WATER; false: HOT_WATER; FALSE: CHILLED_WATER; FALSE: HOT_WATER; FALSE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; FALSE: CHILLED_WATER
JSON_PATH:external_fluid_source[1]:id:: | JSON_PATH:external_fluid_source[1]:id:: | JSON_PATH:external_fluid_source[1] | id |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id |  |  | FALSE: Purchased CHW 1; TRUE: Purchased HW; TRUE: Purchased CW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1
JSON_PATH:external_fluid_source[1]:loop:: | JSON_PATH:external_fluid_source[1]:loop:: | JSON_PATH:external_fluid_source[1] | loop |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop |  |  | FALSE: Purchased CHW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1
JSON_PATH:external_fluid_source[1]:type:: | JSON_PATH:external_fluid_source[1]:type:: | JSON_PATH:external_fluid_source[1] | type |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type |  |  | FALSE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER
JSON_PATH:heat_rejections[0]:id:: | JSON_PATH:heat_rejections[0]:id:: | JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
JSON_PATH:heat_rejections[0]:loop:: | JSON_PATH:heat_rejections[0]:loop:: | JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
JSON_PATH:heat_rejections[0]:type:: | JSON_PATH:heat_rejections[0]:type:: | JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
JSON_PATH:heat_rejections[0]:design_water_flowrate:: | JSON_PATH:heat_rejections[0]:design_water_flowrate:: | JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
JSON_PATH:heat_rejections[0]:fan_speed_control:: | JSON_PATH:heat_rejections[0]:fan_speed_control:: | JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
JSON_PATH:heat_rejections[0]:range:: | JSON_PATH:heat_rejections[0]:range:: | JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
JSON_PATH:heat_rejections[0]:reset_type:: | JSON_PATH:heat_rejections[0]:reset_type:: | JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
JSON_PATH:heat_rejections[1]:id:: | JSON_PATH:heat_rejections[1]:id:: | JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
JSON_PATH:heat_rejections[1]:loop:: | JSON_PATH:heat_rejections[1]:loop:: | JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop
JSON_PATH:heat_rejections[1]:type:: | JSON_PATH:heat_rejections[1]:type:: | JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type
JSON_PATH:pumps[0]:id:: | JSON_PATH:pumps[0]:id:: | JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id |  |  | true: Boiler Pump 1; false: HW Pump 1; false: HW Pump 1; TRUE: Boiler Pump 1; TRUE: HW Pump 1; TRUE: HW Pump 1; TRUE: Boiler Pump 1; TRUE: Boiler Pump 1; TRUE: HW Pump 1; TRUE: HW Pump 1; TRUE: Boiler Pump 1; TRUE: Boiler Pump 1; TRUE: HW Pump 1; TRUE: HW Pump 1; TRUE: HW Pump 1; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: HW Pump 1; TRUE: HW Pump 1; TRUE: Boiler Pump 1; TRUE: Boiler Pump 1; TRUE: Boiler Pump 1; TRUE: Boiler Pump 1; TRUE: HW Pump 1; TRUE: Chiller Pump 1; TRUE: Chiller Pump 1
JSON_PATH:pumps[0]:loop_or_piping:: | JSON_PATH:pumps[0]:loop_or_piping:: | JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping |  |  | true: Boiler Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1
JSON_PATH:pumps[0]:speed_control:: | JSON_PATH:pumps[0]:speed_control:: | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | true: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED
JSON_PATH:pumps[0]:design_electric_power:: | JSON_PATH:pumps[0]:design_electric_power:: | JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[0]:design_flow:: | JSON_PATH:pumps[0]:design_flow:: | JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[0]:design_head:: | JSON_PATH:pumps[0]:design_head:: | JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
JSON_PATH:pumps[0]:motor_efficiency:: | JSON_PATH:pumps[0]:motor_efficiency:: | JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
JSON_PATH:pumps[0]:impeller_efficiency:: | JSON_PATH:pumps[0]:impeller_efficiency:: | JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
JSON_PATH:pumps[1]:id:: | JSON_PATH:pumps[1]:id:: | JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id |  |  | true: Chiller Pump 1; false: HW Pump 2; false: HW Pump 2; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Secondary CHW Pump; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Chiller Pump 1; TRUE: CHW Pump 1; TRUE: Chiller Pump 1; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump
JSON_PATH:pumps[1]:loop_or_piping:: | JSON_PATH:pumps[1]:loop_or_piping:: | JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping |  |  | true: Chiller Loop 1; false: Purchased HW Loop 1; false: Purchased HW Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1
JSON_PATH:pumps[1]:speed_control:: | JSON_PATH:pumps[1]:speed_control:: | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control |  |  | true: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: VARIABLE_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: FIXED_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED
JSON_PATH:pumps[1]:design_electric_power:: | JSON_PATH:pumps[1]:design_electric_power:: | JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[1]:design_flow:: | JSON_PATH:pumps[1]:design_flow:: | JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[2]:id:: | JSON_PATH:pumps[2]:id:: | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id |  |  | true: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump
JSON_PATH:pumps[2]:loop_or_piping:: | JSON_PATH:pumps[2]:loop_or_piping:: | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping |  |  | true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1
JSON_PATH:pumps[2]:speed_control:: | JSON_PATH:pumps[2]:speed_control:: | JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control |  |  | true: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED
JSON_PATH:fluid_loops[0]:id:: | JSON_PATH:fluid_loops[0]:id:: | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased CHW Loop 1 |  | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Boiler Loop 1
JSON_PATH:fluid_loops[0]:type:: | JSON_PATH:fluid_loops[0]:type:: | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  |  | COOLING | HEATING | COOLING |  | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING |  | COOLING | COOLING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | COOLING | COOLING | HEATING
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:id: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:id: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_supply_temperature: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_supply_temperature: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_return_temperature: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_return_temperature: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:temperature_reset_type: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:temperature_reset_type: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:minimum_flow_fraction: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:minimum_flow_fraction: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
JSON_PATH:fluid_loops[0]:child_loops[0]:id: | JSON_PATH:fluid_loops[0]:child_loops[0]:id: | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id |  |  | TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1
JSON_PATH:fluid_loops[0]:child_loops[0]:type: | JSON_PATH:fluid_loops[0]:child_loops[0]:type: | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type |  |  | TRUE: COOLING; TRUE: COOLING; TRUE: COOLING
#N/A | JSON_PATH:fluid_loops[0]:child_loops[0]:: | JSON_PATH:fluid_loops[0] | child_loops[0] |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | child_loops
#N/A | JSON_PATH:fluid_loops[0]:pump_power_per_flow_rate:: | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:id: | JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id |  |  | false: DAC 1; FALSE: DAC1
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:is_sized_using_coincident_load: | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:temperature_reset_type: | JSON_PATH:fluid_loops[0] | heating_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:design_supply_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:design_return_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:outdoor_high_for_loop_supply_reset_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_high_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_high_for_loop_supply_reset_temperature
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:outdoor_low_for_loop_supply_reset_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_low_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_low_for_loop_supply_reset_temperature
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:minimum_flow_fraction: | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction |  |  | FALSE: 0.25
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:flow_control: | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | flow_control
#N/A | JSON_PATH:fluid_loops[0]:heating_design_and_control:operation: | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | operation
JSON_PATH:fluid_loops[1]:id:: | JSON_PATH:fluid_loops[1]:id:: | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  | true: Chiller Loop 1; FALSE: Purchased CHW 1; FALSE: Purchased CHW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chiller Loop 1; FALSE: Purchased CHW Loop 1
JSON_PATH:fluid_loops[1]:type:: | JSON_PATH:fluid_loops[1]:type:: | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  | true: COOLING; FALSE: COOLING; FALSE: COOLING; TRUE: HEATING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; FALSE: COOLING
JSON_PATH:fluid_loops[1]:child_loops[0]:id: | JSON_PATH:fluid_loops[1]:child_loops[0]:id: | JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id |  |  | true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1
JSON_PATH:fluid_loops[1]:child_loops[0]:type: | JSON_PATH:fluid_loops[1]:child_loops[0]:type: | JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type |  |  | true: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::
#N/A | :::

## Templates_OLD
key1 | key2 | key3 | key4 | data_group | object_id | parent_id | data_element | unit_type | units | System_7_VAV_HW_Reheat | PurchasedWater | Boiler | rule-21-1-a | rule-21-1-b | rule-21-2-a | rule-21-2-b | System_2_PTHP
id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
calendar | is_leap_year |  |  | Calendar | N/A | ASHRAE229 1 | is_leap_year
ruleset_model_instances[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | VAV Air Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | Terminal 1 | PTHP Terminal 1
JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | false | false | false | false | false | false | FALSE
JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | HOT_WATER | [6 empty] | CONSTANT_AIR_VOLUME
JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | VARIABLE_AIR_VOLUME | [6 empty] | PTHP 1
JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1
JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | HOT_WATER
JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | Boiler Loop 1
JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id |  |  | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2
JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id |  |  | VAV Air Terminal 2 | Terminal 2 | Terminal 2 | Terminal 2 | Terminal 2 | Terminal 2 | Terminal 2
JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | true | false | false | false | false | false | false
JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER
JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type |  |  | VARIABLE_AIR_VOLUME
JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1
JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER
JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  | Boiler Loop 1
JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System 7 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1 | AHU_HW_System1
JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  |  | HHW Coil 1 | HHW Coil 1 | Heating System 1 | Heating System 1 | Heating System 1 | Heating System 1
JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | PTHP 1
JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop |  |  |  | Purchased HW Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | HP Cooling Coil 1
JSON_PATH:preheat_system | id |  |  | HeatingSystem | Heating System 2 | HVAC 1 | id |  |  | Preheat Coil 1 | [6 empty] | DIRECT_EXPANSION
JSON_PATH:preheat_system | heating_system_type |  |  | HeatingSystem | Heating System 2 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP
JSON_PATH:preheat_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1 | [6 empty] | HP Heating Coil 1
JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1 | [6 empty] | HEAT_PUMP
JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE
JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1
JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1
JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 |  | Boiler 1
JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 |  | Boiler Loop 1
JSON_PATH:boilers[0] | draft_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type |  |  |  |  | NATURAL |  |  |  |  | CAV Fan System 1
JSON_PATH:boilers[0] | rated_capacity |  |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr |  |  | 400000 |  |  |  |  | CONSTANT
JSON_PATH:boilers[0] | efficiency |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency | [9 empty] | Supply Fan 1
JSON_PATH:boilers[0] | efficiency_metric |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric
JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS
JSON_PATH:boilers[0] | operation_lower_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit
JSON_PATH:boilers[0] | operation_upper_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit
JSON_PATH:boilers[1] | id |  |  | Boiler | Boiler 2 | ASHRAE229 1 | id
JSON_PATH:boilers[1] | loop |  |  | Boiler | Boiler 2 | ASHRAE229 1 | loop
JSON_PATH:boilers[1] | draft_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
JSON_PATH:boilers[1] | design_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
JSON_PATH:boilers[1] | energy_source_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
JSON_PATH:boilers[1] | operation_lower_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit
JSON_PATH:boilers[1] | operation_upper_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit
JSON_PATH:boilers[2] | id |  |  | Boiler | Boiler 3 | ASHRAE229 1 | id
JSON_PATH:boilers[2] | loop |  |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
JSON_PATH:boilers[2] | design_capacity |  |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | Chiller 1
JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | Chiller Loop 1
JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | CHW Coil 1
JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | FLUID_LOOP
JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  | Secondary CHW Loop 1
JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  |  | Purchased HW 1 |  | Purchased HW 1 |  | Purchased HW 1 | Purchased HW 1
JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  |  | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  |  | HOT_WATER |  | HOT_WATER |  | HOT_WATER | HOT_WATER
JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id |  |  | Boiler Pump 1 |  |  |  |  | HW Pump 1 | HW Pump 1
JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping |  |  | Boiler Loop 1 |  |  |  |  | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED
JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id |  |  | Chiller Pump 1 |  |  |  |  | HW Pump 2 | HW Pump 2
JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping |  |  | Chiller Loop 1 |  |  |  |  | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED
JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id |  |  | Secondary CHW Pump
JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping |  |  | Secondary CHW Loop 1
JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control |  |  | VARIABLE_SPEED
JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING
JSON_PATH:fluid_loops[0] | child_loops[0] |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | child_loops
JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate
JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id |  |  |  | DAC 1
JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load
JSON_PATH:fluid_loops[0] | heating_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_high_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_high_for_loop_supply_reset_temperature
JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_low_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_low_for_loop_supply_reset_temperature
JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | flow_control
JSON_PATH:fluid_loops[0] | heating_design_and_control | operation |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | operation
JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  | Chiller Loop 1
JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  | COOLING
JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id |  |  | Secondary CHW Loop 1
JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type |  |  | COOLING

## TCDs_old
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | rule-21-3-a | rule-21-3-b | rule-21-4-a | rule-21-4-b | rule-21-5-a | rule-21-5-b | rule-21-5-c | rule-21-5-d | rule-21-6-a | rule-21-6-b | rule-21-6-c | rule-21-7-a | rule-21-7-b | rule-21-9-a | rule-21-9-b | rule-21-10-a | rule-21-10-b | rule-21-10-c | rule-21-10-d | rule-21-11-a | rule-21-11-b | rule-21-12-a | rule-21-12-b | rule-21-13-a | rule-21-13-b | rule-21-16-a | rule-21-16-b | rule-21-17-a | rule-21-17-b | rule-21-17-c | rule-21-17-d | rule-21-17-e | rule-21-17-f | rule-21-18-a | rule-21-18-b | rule-21-18-c
Section | [10 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Rule | [10 empty] | 3 | 3 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 7 | 7 | 9 | 9 | 10 | 10 | 10 | 10 | 11 | 11 | 12 | 12 | 13 | 13 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18
Test | [10 empty] | a | b | a | b | a | b | c | d | a | b | c | a | b | a | b | a | b | c | d | a | b | a | b | a | b | a | b | a | b | c | d | e | f | a | b | c
Notes
test_description | [10 empty] | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler. The baseline building's hot water system's sizing is based on coincident loads. Expected result: PASS | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler. The baseline building's hot water system's sizing is NOT based on coincident loads. Expected result: FAIL | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler and is correctly modeled with a natural draft boiler. Expected result: PASS | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler and is incorrectly modeled with a forced draft boiler. Expected result: FAIL | Baseline building is 12,000 ft2, has baseline system type 7 and is correctly modeled with a HW Loop with a single boiler. | Baseline building is 12,000 ft2, has baseline system type 7 and is incorrectly modeled with a HW Loop with two boilers. | Baseline building is 24,000 ft2, has baseline system type 7 and is correctly modeled with a HW Loop with two equally sized boiler(s). | Baseline building is 24,000 ft2, has baseline system type 7 and is incorrectly modeled with a HW Loop with two unequally sized boiler(s). | Baseline RMR has utilizes system 7 with two boilers staged based on load. Boiler 1 is staged before Boiler 2. | Baseline RMR has utilizes system 7 with two boilers staged based on load. Boiler 2 is staged before Boiler 1. | Baseline RMR has utilizes system 7 with two boilers is not staged based on load. | Baseline RMR has utilizes system 7 with supply and return temperatures correctly set to 180 F and 130 F respectively | Baseline RMR has utilizes system 7 with supply and return temperatures incorrectly set to 200 F and 150 F respectively | Baseline RMR has utilizes system 7 with total pump power per flow rate correctly set to 19 W/gpm | Baseline RMR has utilizes system 7 with total pump power per flow rate incorrectly set to 21 W/gpm | Baseline RMR has HHW plant with the hot water pump that serves a total of 100,000 ft2 floor area. The pump's speed control value is correctly set to FIXED_SPEED | Baseline RMR has HHW plant with the hot water pump that serves a total of 100,000 ft2 floor area. The pump's speed control value is incorrectly set to VARIABLE_SPEED | Baseline RMR has HHW plant with the hot water pump that serves a total of 130,000 ft2 floor area. The pump's speed control value is correctly set to VARIABLE_SPEED | Baseline RMR has HHW plant with the hot water pump that serves a total of 130,000 ft2 floor area. The pump's speed control value is incorrectly set to FIXED_SPEED | Baseline RMR has system 7 with child loop value correctly set to null | Baseline RMR has system 7 with child loop incorrectly referencing to FluidLoop 2 | Baseline RMR has system 7 with flow control and operation correctly | Baseline RMR has system 7 with flow control and operation incorrectly | Baseline RMR has system 7 with heating design and control's minimum flow fraction correctly set to 0.25 | Baseline RMR has system 7 with heating design and control's minimum flow fraction incorrectly set to 0.30 | Baseline RMR has system 7 with a single heating loop | Baseline RMR has system 7 with more than one heating loop | Baseline RMR has system 7 with < 300 kBtu/hr, has AFUE equal to 80% as per Tables G3.5.6 | Baseline RMR has system 7 with < 300 kBtu/hr, AFUE does not equal 80% as per Tables G3.5.6 | Baseline RMR has system 7 with greater than 300 kBtu/hr but less than 2,500 kBtu/hr, has thermal efficiency equal to 75% as per Tables G3.5.6 | Baseline RMR has system 7 with greater than 300 kBtu/hr but less than 2,500 kBtu/hr, thermal efficiency does not equal 75% as per Tables G3.5.6 | Baseline RMR has system 7 with greater than 2,500 kBtu/hr, has combustion efficiency equal to 80% as per Tables G3.5.6 | Baseline RMR has system 7 with greater than 2,500 kBtu/hr, combustion efficiency does not equal 80% as per Tables G3.5.6 | System 7 is correctly modeled with a natural gas boiler | System 7 is incorrectly modeld an electric boiler | A purchased hot water system does not have an applicable fuel type
expected_rule_outcome | [10 empty] | pass | fail | pass | fail | pass | fail | pass | fail | pass | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | pass | fail | not_applicable
standard | rule_id | [9 empty] | 21-3 | 21-3 | 21-4 | 21-4 | 21-5 | 21-5 | 21-5 | 21-5 | 21-6 | 21-6 | 21-6 | 21-7 | 21-7 | 21-9 | 21-9 | 21-10 | 21-10 | 21-10 | 21-10 | 21-11 | 21-11 | 21-12 | 21-12 | 21-13 | 21-13 | 21-16 | 21-16 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-18 | 21-18 | 21-18
standard | ruleset_reference | [9 empty] | G3.1.2.2 | G3.1.2.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.3 | G3.1.3.3 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.2 | G3.1.3.2 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1
standard | rule_description | [9 empty] | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | Baseline shall have only one heating hot water plant. | Baseline shall have only one heating hot water plant. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel.
standard | applicable_rmr | [9 empty] | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR
standard | rule_assertion | bar: a to c
standard | comparison_value | [9 empty] | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value
standard | primary_rule | [9 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
standard | schema_version | [9 empty] | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23
template_lookup | [10 empty] | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | PurchasedWater
rmr_template | user
rmr_template | proposed
rmr_template | baseline | [9 empty] | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true
rmr_template | json_template | id |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  | Calendar | N/A | ASHRAE229 1 | is_leap_year
rmr_template | json_template | ruleset_model_instances[0] | id |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
rmr_template | json_template | JSON_PATH:buildings[0] | id |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
rmr_template | json_template | JSON_PATH:buildings[0] | building_open_schedule |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id | Space | Space 1 | Zone 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area | Space | Space 1 | Zone 1 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id | Air Terminal | Terminal 1 | Zone 1 | id |  |  | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | false
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_source | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_from_loop | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type | Air Terminal | Terminal 1 | Zone 1 | type |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | AHU_HW_System1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_source | Air Terminal | Terminal 1 | Zone 1 | heating_source
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan | Fan | Fan 1 | Terminal 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan_configuration | Air Terminal | Terminal 1 | Zone 1 | fan_configuration
rmr_template | json_template | JSON_PATH:zones[1] | id |  | Zone | Zone 2 | Building Segment 1 | id |  |  | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id | Space | Space 2 | Zone 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area | Space | Space 2 | Zone 2 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id | Air Terminal | Terminal 2 | Zone 2 | id |  |  | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | Terminal 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | false
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type | Air Terminal | Terminal 2 | Zone 2 | type |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | AHU_HW_System1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_from_loop | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan | Fan | Fan 2 | Terminal 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan_configuration | Air Terminal | Terminal 2 | Zone 2 | fan_configuration
rmr_template | json_template | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | AHU_HW_System1
rmr_template | json_template | JSON_PATH:heating_system | id |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | c: HHW Coil 1
rmr_template | json_template | JSON_PATH:heating_system | heating_system_type |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | c: FLUID_LOOP
rmr_template | json_template | JSON_PATH:heating_system | energy_source_type |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop |  |  | c: Purchased HW Loop 1
rmr_template | json_template | JSON_PATH:preheat_system | id |  | HeatingSystem | Heating System 2 | HVAC 1 | id |  |  | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1
rmr_template | json_template | JSON_PATH:preheat_system | heating_system_type |  | HeatingSystem | Heating System 2 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
rmr_template | json_template | JSON_PATH:preheat_system | hot_water_loop |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_system | id |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1
rmr_template | json_template | JSON_PATH:fan_system | fan_control |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE
rmr_template | json_template | JSON_PATH:fan_system | supply_fans[0] | id | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
rmr_template | json_template | JSON_PATH:fan_system | return_fans[0] | id | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
rmr_template | json_template | JSON_PATH:boilers[0] | id |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1
rmr_template | json_template | JSON_PATH:boilers[0] | loop |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:boilers[0] | draft_type |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type
rmr_template | json_template | JSON_PATH:boilers[0] | rated_capacity |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:boilers[0] | efficiency |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency
rmr_template | json_template | JSON_PATH:boilers[0] | efficiency_metric |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric
rmr_template | json_template | JSON_PATH:boilers[0] | energy_source_type |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS
rmr_template | json_template | JSON_PATH:boilers[0] | operation_lower_limit |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit
rmr_template | json_template | JSON_PATH:boilers[0] | operation_upper_limit |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit
rmr_template | json_template | JSON_PATH:boilers[1] | id |  | Boiler | Boiler 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:boilers[1] | loop |  | Boiler | Boiler 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:boilers[1] | draft_type |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
rmr_template | json_template | JSON_PATH:boilers[1] | design_capacity |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:boilers[1] | energy_source_type |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:boilers[1] | operation_lower_limit |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit
rmr_template | json_template | JSON_PATH:boilers[1] | operation_upper_limit |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit
rmr_template | json_template | JSON_PATH:boilers[2] | id |  | Boiler | Boiler 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:boilers[2] | loop |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:boilers[2] | design_capacity |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:chillers[0] | id |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1
rmr_template | json_template | JSON_PATH:chillers[0] | cooling_loop |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1
rmr_template | json_template | JSON_PATH:chillers[0] | design_capacity |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[0] | energy_source_type |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:chillers[0] | full_load_efficiency |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
rmr_template | json_template | JSON_PATH:chillers[0] | compressor_type |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
rmr_template | json_template | JSON_PATH:chillers[1] | id |  | Chiller | Chiller 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[1] | cooling_loop |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[1] | design_capacity |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[2] | id |  | Chiller | Chiller 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[2] | cooling_loop |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[2] | design_capacity |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[3] | id |  | Chiller | Chiller 4 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[3] | cooling_loop |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[3] | design_capacity |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:cooling_system | id |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1
rmr_template | json_template | JSON_PATH:cooling_system | cooling_system_type |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
rmr_template | json_template | JSON_PATH:cooling_system | chilled_water_loop |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | id |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  | c: Purchased HW 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | loop |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  | c: Purchased HW Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | type |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  | c: HOT_WATER
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | id |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | loop |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | type |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | id |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[0] | loop |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[0] | type |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_water_flowrate |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | fan_speed_control |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
rmr_template | json_template | JSON_PATH:heat_rejections[0] | range |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
rmr_template | json_template | JSON_PATH:heat_rejections[0] | reset_type |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
rmr_template | json_template | JSON_PATH:heat_rejections[1] | id |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
rmr_transformations | user | JSON_PATH:boilers[0] | id |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | proposed | JSON_PATH:boilers[0] | id |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:climate_zone |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone |  |  | a: CZ4A; b: CZ4A; c: CZ4A; d: CZ4A
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | id | Space | Space 1 | Zone 1 | id |  |  | a: Space 1; b: Space 1; c: Space 1; d: Space 1; a: Space 1; b: Space 1; a: Space 1; b: Space 1; c: Space 1; d: Space 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | floor_area | Space | Space 1 | Zone 1 | floor_area | area | ft2 | a: 6000; b: 6000; c: 12000; d: 12000; a: 24000; b: 24000; a: 60000; b: 60000; c: 70000; d: 70000
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | id | Space | Space 1 | Zone 2 | id |  |  | a: Space 2; b: Space 2; c: Space 2; d: Space 2; a: Space 2; b: Space 2; a: Space 2; b: Space 2; c: Space 2; d: Space 2
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | floor_area | Space | Space 1 | Zone 2 | floor_area | area | ft2 | a: 6000; b: 6000; c: 12000; d: 12000; a: 6000; b: 6000; a: 40000; b: 40000; c: 70000; d: 70000
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule | Space | Space 1 | Zone 2 | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:surfaces[0] | id |  | Surface | Surface 1 | Zone 1 | id
rmr_transformations | baseline | JSON_PATH:surfaces[0] | adjacent_to |  | Surface | Surface 1 | Zone 1 | adjacent_to
rmr_transformations | baseline | JSON_PATH:surfaces[0] | tilt |  | Surface | Surface 1 | Zone 1 | tilt
rmr_transformations | baseline | JSON_PATH:surfaces[0] | area |  | Surface | Surface 1 | Zone 1 | area | area | ft2
rmr_transformations | baseline | JSON_PATH:surfaces[0] | construction | id | Construction | Construction 1 | Surface 1 | id
rmr_transformations | baseline | JSON_PATH:surfaces[0] | construction | u_factor | Construction | Construction 1 | Surface 1 | u_factor | thermal_transmittance | Btu/hr-ft2-R
rmr_transformations | baseline | JSON_PATH:boilers[0] | id |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[0] | loop |  | Boiler | Boiler 1 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[0] | draft_type |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type |  |  | a: NATURAL; b: FORCED
rmr_transformations | baseline | JSON_PATH:boilers[0] | rated_capacity |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr | a: 400000; b: 400000; c: 400000; d: 400000; a: 40000; b: 80000; c: 20000; a: 250000; b: 250000; c: 500000; d: 500000; e: 3000000; f: 3000000
rmr_transformations | baseline | JSON_PATH:boilers[0] | efficiency |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency |  |  | a: 0.8; b: 0.75; c: 0.75; d: 0.7; e: 0.8; f: 0.85
rmr_transformations | baseline | JSON_PATH:boilers[0] | efficiency_metric |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric |  |  | a: ANNUAL_FUEL_UTILIZATION; b: ANNUAL_FUEL_UTILIZATION; c: THERMAL; d: THERMAL; e: COMBUSTION; f: COMBUSTION
rmr_transformations | baseline | JSON_PATH:boilers[0] | energy_source_type |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | b: ELECTRICITY
rmr_transformations | baseline | JSON_PATH:boilers[0] | operation_lower_limit |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit | capacity | Btu/hr | a: 0; b: 35000; c: 0
rmr_transformations | baseline | JSON_PATH:boilers[0] | operation_upper_limit |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit | capacity | Btu/hr | a: 40000; b: 115000; c: 40000
rmr_transformations | baseline | JSON_PATH:boilers[1] | id |  | Boiler | Boiler 2 | ASHRAE229 1 | id |  |  | b: Boiler 2; c: Boiler 2; d: Boiler 2; a: Boiler 2; b: Boiler 2; c: Boiler 2
rmr_transformations | baseline | JSON_PATH:boilers[1] | loop |  | Boiler | Boiler 2 | ASHRAE229 1 | loop |  |  | b: Boiler Loop 1; c: Boiler Loop 1; d: Boiler Loop 1; a: Boiler Loop 1; b: Boiler Loop 1; c: Boiler Loop 1
rmr_transformations | baseline | JSON_PATH:boilers[1] | draft_type |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
rmr_transformations | baseline | JSON_PATH:boilers[1] | rated_capacity |  | Boiler | Boiler 2 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr | b: 600000; c: 400000; d: 800000; a: 35000; b: 35000; c: 35000
rmr_transformations | baseline | JSON_PATH:boilers[1] | energy_source_type |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
rmr_transformations | baseline | JSON_PATH:boilers[1] | operation_lower_limit |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit | capacity | Btu/hr | a: 40000; b: 0; c: 0
rmr_transformations | baseline | JSON_PATH:boilers[1] | operation_upper_limit |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit | capacity | Btu/hr | a: 75000; b: 35000; c: 35000
rmr_transformations | baseline | JSON_PATH:boilers[1] | design_capacity |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[2] | id |  | Boiler | Boiler 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[2] | loop |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[2] | rated_capacity |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | id |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | loop |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | type |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | id |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | id |  |  | a: Boiler Loop 1; b: Boiler Loop 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | type |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate | power_per_volumetric_flow_rate | W/gpm | a: 19; b: 21
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | id | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | id |  |  | b: Secondary HW Loop 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | type | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | type |  |  | b: HEATING
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | id | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id |  |  | a: DAC 1; b: DAC 1; a: DAC 1; b: DAC 1; a: DAC 1; b: DAC 1; a: DAC 1; b: DAC 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load |  |  | a: true; b: false
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F | a: 180; b: 200
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F | a: 130; b: 150
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control | FluidLoopDesignAndControl | Loop 1 | Loop 1 | flow_control |  |  | a: VARIABLE_FLOW; b: FIXED_FLOW
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation | FluidLoopDesignAndControl | Loop 1 | Loop 1 | operation |  |  | a: CONTINUOUS; b: INTERMITTENT
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction | FluidLoopDesignAndControl | Loop 1 | Loop 1 | minimum_flow_fraction |  |  | a: 0.25; b: 0.3
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | id |  | FluidLoopDesignAndControl | Loop 2 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | type |  | FluidLoopDesignAndControl | Loop 2 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:pumps[0] | speed_control |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | a: FIXED_SPEED; b: VARIABLE_SPEED; c: VARIABLE_SPEED; d: FIXED_SPEED
rmr_transformations | baseline | JSON_PATH:pumps[1] | speed_control |  | Pump | Pump 2 | ASHRAE229 1 | speed_control
rmr_transformations | baseline | JSON_PATH:pumps[2] | id |  | Pump | Pump 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:pumps[2] | loop_or_piping |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping
rmr_transformations | baseline | JSON_PATH:heating_system | id |  | HeatingSystem | Heating System 1 | HVAC 1 | id
rmr_transformations | baseline | JSON_PATH:heating_system | heating_system_type |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type
rmr_transformations | baseline | JSON_PATH:heating_system | hot_water_loop |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop
rmr_transformations | baseline | JSON_PATH:cooling_system | id |  | CoolingSystem | Cooling System 1 | HVAC 1 | id
rmr_transformations | baseline | JSON_PATH:cooling_system | design_sensible_cool_capacity |  | CoolingSystem | Cooling System 1 | HVAC 1 | design_sensible_cool_capacity | cooling_capacity | ton | a: 7; b: 7; c: 7; d: 7
rmr_transformations | baseline | JSON_PATH:preheat_system | design_capacity |  | HeatingSystem | Heating System 1 | HVAC 1 | design_capacity | capacity | Btu/hr | a: 20000; b: 20000; c: 20000; d: 20000
rmr_transformations | baseline | JSON_PATH:fluid_loops[2] | id |  | FluidLoopDesignAndControl | Loop 3 | ASHRAE229 1 | id |  |  | b: Boiler Loop 2
rmr_transformations | baseline | JSON_PATH:fluid_loops[2] | type |  | FluidLoopDesignAndControl | Loop 3 | ASHRAE229 1 | type |  |  | b: HEATING

## TCDs
key1 | key2 | key3 | key4 | key5 | key6 | data_group | object_id | parent_id | data_element | unit_type | units | rule-21-3-a | rule-21-3-b | rule-21-3-c | rule-21-3-d | rule-21-3-e | rule-21-4-a | rule-21-4-b | rule-21-4-c | rule-21-4-d | rule-21-4-e | rule-21-5-a | rule-21-5-b | rule-21-5-c | rule-21-5-d | rule-21-5-e | rule-21-5-f | rule-21-6-a | rule-21-6-b | rule-21-6-c | rule-21-6-d | rule-21-6-e | rule-21-6-f | rule-21-6-g | rule-21-7-a | rule-21-7-b | rule-21-7-c | rule-21-7-d | rule-21-7-e | rule-21-7-f | rule-21-7-g | rule-21-9-a | rule-21-9-b | rule-21-9-c | rule-21-9-d | rule-21-9-e | rule-21-10-a | rule-21-10-b | rule-21-10-c | rule-21-10-d | rule-21-10-e | rule-21-11-a | rule-21-11-b | rule-21-11-c | rule-21-11-d | rule-21-11-e | rule-21-12-a | rule-21-12-b | rule-21-12-c | rule-21-12-d | rule-21-12-e | rule-21-12-f | rule-21-12-g | rule-21-13-a | rule-21-13-b | rule-21-13-c | rule-21-13-d | rule-21-13-e | rule-21-16-a | rule-21-16-b | rule-21-16-c | rule-21-16-d | rule-21-16-e | rule-21-17-a | rule-21-17-b | rule-21-17-c | rule-21-17-d |  | rule-21-17-f | rule-21-17-g | rule-21-17-h | rule-21-17-i | rule-21-17-i | rule-21-18-a | rule-21-18-b | rule-21-18-c | rule-21-18-d | rule-21-18-e | rule-21-18-f | rule-21-18-g
Section | [11 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Rule | [11 empty] | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Test | [11 empty] | a | b | c | d | e | a | b | c | d | e | a | b | c | d | e | f | a | b | c | d | e | f | g | a | b | c | d | e | f | g | a | b | c | d | e | a | b | c | d | e | a | b | c | d | e | a | b | c | d | e | f | g | a | b | c | d | e | a | b | c | d | e | a | b | c | d | e | f | g | h | i | i | a | b | c | d | e | f | g
Notes
test_description | [11 empty] | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler. The baseline building's hot water system's sizing is based on coincident loads. Expected result: PASS | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler. The baseline building's hot water system's sizing is NOT based on coincident loads. Expected result: FAIL | The project consists of one building segment with one zone. Space conditioning is provided by system type 5 with boiler. The baseline building's hot water system's sizing is based on coincident loads. Expected result: PASS | The project consists of one building segment with one zone. Space conditioning is provided by system type 5 with boiler. The baseline building's hot water system's sizing is NOT based on coincident loads. Expected result: FAIL | The project consists of one building segment with one zone. Space conditioning is provided by system type 2. Expected result: UNDETERMINED | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler and is correctly modeled with a natural draft boiler. Expected result: PASS | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler and is incorrectly modeled with a forced draft boiler. Expected result: FAIL | The project consists of one building segment with one zone. Space conditioning is provided by system type 11.2 with boiler and is correctly modeled with a natural draft boiler. Expected result: PASS | The project consists of one building segment with one zone. Space conditioning is provided by system type 11.2 with boiler and is incorrectly modeled with a forced draft boiler. Expected result: FAIL | The project consists of one building segment with one zone. Space conditioning is provided by system type 3 with no hot water loops. Expected result: NOT APPLICABLE | The project consists of one building segment with two zones and two spaces. Building is 12,000 ft2, has baseline system type 7 and is correctly modeled with a HW Loop with a single boiler. Expected result: PASS | The project consists of one building segment with two zones and two spaces. Building is 12,000 ft2, has baseline system type 7 and is incorrectly modeled with a HW Loop with two boilers. Expected result: FAIL | The project consists of one building segment with one zone and one space. Building is 24,000 ft2, has baseline system type 12 and is correctly modeled with a HW Loop with two equally sized boiler(s). Expected result: PASS | The project consists of one building segment with one zone and one space. Building is 24,000 ft2, has baseline system type 12 and is incorrectly modeled with a HW Loop with two unequally sized boiler(s). Expected result: FAIL | The project consists of one building segment with one zone and one space. Building is 24,000 ft2, has baseline system type 12 and is incorrectly modeled with a HW Loop with one boiler. Expected result: FAIL | The project consists of one building segment with one zone and one space. Building is 24,000 ft2, has baseline system type 4. Expected result: Not Applicable | The project consists of one building segment with two zones and two spaces. Baseline RMD has utilizes system 7 with two boilers staged based on load. Boiler 1 is staged before Boiler 2. Expected result: PASS | The project consists of one building segment with two zones and two spaces. Baseline RMD has utilizes system 7 with two boilers staged based on load. Boiler 2 is staged before Boiler 1. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has utilizes system 7 with two boilers is not staged based on load. Expected result: FAIL | The project consists of one building segment with two zones and two spaces. Baseline RMD has utilizes system 1 with two boilers staged based on load. Boiler 1 is staged before Boiler 2. Expected result: PASS | The project consists of one building segment with two zones and two spaces. Baseline RMD has utilizes system 1 with two boilers staged based on load. Boiler 2 is staged before Boiler 1. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has utilizes system 1 with two boilers is not staged based on load. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has utilizes system 6. Expected result: NOT APPLICABLE | The project consists of one building segment with two zones and two spaces. Baseline RMD utilizes system 7 with supply and return temperatures correctly set to 180 F and 130 F respectively. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has utilizes system 7 with supply and return temperatures incorrectly set to 200 F and correctly set to 130 F respectively. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has utilizes system 7 with supply and return temperatures correctly set to 180 F and inccorectly to 150 F respectively. Expected result: FAIL | The project consists of one building segment with two zones and two spaces. Baseline RMD utilizes system 5 with supply and return temperatures correctly set to 180 F and 130 F respectively. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has utilizes system 5 with supply and return temperatures incorrectly set to 200 F and correctly set to 130 F respectively. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has utilizes system 5 with supply and return temperatures correctly set to 180 F and inccorectly to 150 F respectively. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has utilizes system 5b. Expected result: Not Applicable | The project consists of one building segment with two zones. Baseline RMD utilizes system 7 with total pump power per flow rate correctly set to 19 W/gpm. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD utilizes system 7 with total pump power per flow rate incorrectly set to 21 W/gpm. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMD utilizes system 1a with total pump power per flow rate correctly set to 19 W/gpm. Expected result: PASS | The project consists of one building segment with one zone. Baseline RMD utilizes system 1a with total pump power per flow rate incorrectly set to 21 W/gpm. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMD utilizes system 1b. Expected result: Not Applicable | The project consists of one building segment with two zones and two spaces. Baseline RMD has HHW plant with the hot water pump that serves a total of 100,000 ft2 floor area. The pump's speed control value is correctly set to FIXED_SPEED. Expected result: PASS | The project consists of one building segment with two zones and two spaces. Baseline RMD has HHW plant with the hot water pump that serves a total of 100,000 ft2 floor area. The pump's speed control value is incorrectly set to VARIABLE_SPEED. Expected result: FAIL | The project consists of one building segment with one zone and one space. Baseline RMD has HHW plant with the hot water pump that serves a total of 140,000 ft2 floor area. The pump's speed control value is correctly set to VARIABLE_SPEED. Expected result: PASS | The project consists of one building segment with one zone and one space. Baseline RMD has HHW plant with the hot water pump that serves a total of 140,000 ft2 floor area. The pump's speed control value is incorrectly set to FIXED_SPEED. Expected result: FAIL | The project consists of one building segment with one zone and one space. Baseline RMD system type 8 Expected result: Not Appicable | The project consists of one building segment with two zones. Baseline RMD has system 7 with child loop value correctly set to null. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has system 7 with child loop incorrectly referencing to FluidLoop 2. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMD has system 12a with child loop value correctly set to null. Expected result: PASS | The project consists of one building segment with one zone. Baseline RMD has system 12a with child loop incorrectly referencing to FluidLoop 2. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMD has system 10. Expected result: Not Applicable | The project consists of one building segment with two zones. Baseline RMR has system 7 with flow control and operation correctly. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has system 7 with flow control specified correctly, and operation incorrectly. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has system 7 with flow control specified incorrectly, and operation correctly. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMR has system 1b with flow control and operation correctly. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has system 1b with flow control specified correctly, and operation incorrectly. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has system 1b with flow control specified incorrectly, and operation correctly. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has system 9. Expected result: Not Applicable | The project consists of one building segment with two zones. Baseline RMD has system 7 with heating design and control's minimum flow fraction correctly set to 0.25. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has system 7 with heating design and control's minimum flow fraction incorrectly set to 0.30. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has system 3b with heating design and control's minimum flow fraction correctly set to 0.25. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMD has system 3b with heating design and control's minimum flow fraction incorrectly set to 0.30. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMD has system 11.1a. Expected result: Not Applicable | The project consists of one building segment with two zones. Baseline RMR has system 7 correctly modeled with a single heating loop. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMR has system 7 incorrectly modeled with more than one heating loop. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMR has system 5b correctly modeled with a single heating loop. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMR has system 5b incorrectly modeled with more than one heating loop. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMR has system 11.1. Expected result: Not Applicable | The project consists of one building segment with two zones. Baseline RMR has system 7 with < 300 kBtu/hr, has AFUE equal to 80% as per Tables G3.5.6. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMR has system 7 with < 300 kBtu/hr, has AFUE equal to 80% as per Tables G3.5.6, BUT efficiency_metric is incorrect. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMR has system 7 with < 300 kBtu/hr, AFUE does not equal 80% as per Tables G3.5.6. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMR has system 7 with greater than 300 kBtu/hr but less than 2,500 kBtu/hr, has thermal efficiency equal to 75% as per Tables G3.5.6. Expected result: PASS | The project consists of one building segment with two zones. Baseline RMR has system 7 with greater than 300 kBtu/hr but less than 2,500 kBtu/hr, has thermal efficiency equal to 75% as per Tables G3.5.6, BUT efficiency_metric incorrect. Expected result: FAIL | The project consists of one building segment with two zones. Baseline RMR has system 7 with greater than 300 kBtu/hr but less than 2,500 kBtu/hr, thermal efficiency does not equal 75% as per Tables G3.5.6. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMR has system 12a with greater than 2,500 kBtu/hr, has combustion efficiency equal to 80% as per Tables G3.5.6. Expected result: PASS | The project consists of one building segment with one zone. Baseline RMR has system 12a with greater than 2,500 kBtu/hr, has combustion efficiency equal to 80% as per Tables G3.5.6, BUT efficiency_metric incorrect. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMR has system 12a with greater than 2,500 kBtu/hr, combustion efficiency does not equal 80% as per Tables G3.5.6. Expected result: FAIL | The project consists of one building segment with one zone. Baseline RMR has system 12b. Expected result: Not Applicable | The project consists of one building segment with two zones. System 7 is correctly modeled with a natural gas boiler. Expected result: PASS | The project consists of one building segment with two zones. System 7 is incorrectly modeld an electric boiler. Expected result: FAIL | The project consists of one building segment with two zones. A purchased hot water system does not have an applicable fuel type. Expected result: Not Applicable | The project consists of one building segment with two zones. System 7 is modeld a propane boiler. Expected result: Undetermined | The project consists of one building segment with two zones. System 1 is correctly modeled with a natural gas boiler. Expected result: PASS | The project consists of one building segment with two zones. System 1 is incorrectly modeld an electric boiler. Expected result: FAIL | The project consists of one building segment with two zones. System 1c Expected Result: Not Applicable
expected_rule_outcome | [11 empty] | pass | fail | pass | fail | not_applicable | pass | fail | pass | fail | not_applicable | pass | fail | pass | fail | fail | not_applicable | pass | pass | fail | pass | pass | fail | not_applicable | pass | fail | fail | pass | fail | fail | not_applicable | pass | fail | pass | fail | not_applicable | pass | fail | pass | fail | not_applicable | pass | fail | pass | fail | not_applicable | pass | fail | fail | pass | fail | fail | not_applicable | pass | fail | pass | fail | not_applicable | pass | fail | pass | fail | not_applicable | pass | fail | fail | pass | fail | fail | pass | fail | fail | not_applicable | pass | fail | not_applicable | undetermined | pass | fail | not_applicable
standard | rule_id | [10 empty] | 21-3 | 21-3 | 21-3 | 21-3 | 21-3 | 21-4 | 21-4 | 21-4 | 21-4 | 21-4 | 21-5 | 21-5 | 21-5 | 21-5 | 21-5 | 21-5 | 21-6 | 21-6 | 21-6 | 21-6 | 21-6 | 21-6 | 21-6 | 21-7 | 21-7 | 21-7 | 21-7 | 21-7 | 21-7 | 21-7 | 21-9 | 21-9 | 21-9 | 21-9 | 21-9 | 21-10 | 21-10 | 21-10 | 21-10 | 21-10 | 21-11 | 21-11 | 21-11 | 21-11 | 21-11 | 21-12 | 21-12 | 21-12 | 21-12 | 21-12 | 21-12 | 21-12 | 21-13 | 21-13 | 21-13 | 21-13 | 21-13 | 21-16 | 21-16 | 21-16 | 21-16 | 21-16 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-17 | 21-18 | 21-18 | 21-18 | 21-18 | 21-18 | 21-18 | 21-18
standard | ruleset_reference | [10 empty] | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.2.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.3 | G3.1.3.3 | G3.1.3.3 | G3.1.3.3 | G3.1.3.3 | G3.1.3.3 | G3.1.3.3 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.5 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.3.2 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1 | G3.1.2.1
standard | rule_description | [10 empty] | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When the baseline building is modeled with a hot water or chilled water plant the plant shall be sized based on coincident loads. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When baseline building does not use purchased heat, baseline systems 1,5,7,11,12 shall be modeled with natural draft boilers. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), for building area>15,000ft2, two equally sized boilers should be modeled. Else a single boiler shall be modeled. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), and is modeled with two boilers, each boiler shall be staged based on load. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12), the hot water supply temperature (HWST) shall be 180F, and the hot water return temperature (HSRT) shall be 130F | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building is modeled with a hot water plant, served by boiler(s), (for baseline system type = 1,5,7,11 and 12), the hot water pump power shall be 19W/gpm | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building uses boiler)s) or purchased hot water, the hot water pump shall be modeled as riding the pump curve if the hot water system serves less than 120,000 ft^2 otherwise it shall be modeled with a VFD. | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building users boiler(s) or purchased hot water, the HW loop shall be modeled as primary only | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the HW Loop is modeled with continuous variable flow | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | When the baseline building uses boiler(s) or purchased hot water, the hot water pumping system shall be modeled with a minimum turndown ratio of 0.25. | Baseline shall have only one heating hot water plant. | Baseline shall have only one heating hot water plant. | Baseline shall have only one heating hot water plant. | Baseline shall have only one heating hot water plant. | Baseline shall have only one heating hot water plant. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | All boilers in the baseline building design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Tables G3.5.6. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel. | For baseline building, fossil fuel systems shall be modeled using natural gas as their fuel source. Exception: For fossil fuel systems where natural gas is not available for the proposed building site as determined by the rating authority, the baseline HVAC systems shall be modeled using propane as their fuel.
standard | applicable_rmr | [10 empty] | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR
standard | rule_assertion | bar: a to g
standard | comparison_value | [10 empty] | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value
standard | primary_rule | [10 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
standard | schema_version | [10 empty] | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23
template_lookup | [11 empty] | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_2_PTHP | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_11.2_VAV_SZ | System_11.2_VAV_SZ | System_3_PSZ_AC_Gas_Furnace | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System 12_CAV_SZ_HW | System 12_CAV_SZ_HW | System 12_CAV_SZ_HW | System_4_PSZ_HP | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_1_PTAC | System_1_PTAC | System_1_PTAC | System_6_PVAV_Elec_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5_PVAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | Sys_1a_KJW | Sys_1a_KJW | System_1b_PTAC | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_11.2a_VAV_SZ | System_11.2a_VAV_SZ | System_8_PFP_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System 12a_CAV_SZ_HW | System 12a_CAV_SZ_HW | System_10_Warm_Air_Furnace_Elec | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_1b_PTAC | System_1b_PTAC | System_1b_PTAC | System_9_Warm_Air_Furnace_Gas | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_3b_PSZ_AC_Gas_Furnace | System_3b_PSZ_AC_Gas_Furnace | System_11.1a_VAV_SZ | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_11.1_VAV_SZ | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System 12a_CAV_SZ_HW | System 12a_CAV_SZ_HW | System 12a_CAV_SZ_HW | System 12a_CAV_SZ_HW | System_7_VAV_HW_Reheat | System_7_VAV_HW_Reheat | PurchasedWater | System_7_VAV_HW_Reheat | System_1_PTAC | System_1_PTAC | System_1c_PTAC
rmr_template | user
rmr_template | proposed
rmr_template | baseline | [10 empty] | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true | true
rmr_template | json_template | id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  |  | Calendar | N/A | ASHRAE229 1 | is_leap_year
rmr_template | json_template | ruleset_model_instances[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
rmr_template | json_template | JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
rmr_template | json_template | JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTHP Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTAC Terminal 1a | PTAC Terminal 1a | PTAC Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Terminal 1 | VAV Air Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | true | TRUE | TRUE | FALSE | true | true | TRUE | TRUE | TRUE | true | true | TRUE | TRUE | TRUE | TRUE | true | true | true | FALSE | FALSE | FALSE | TRUE | true | true | true | TRUE | TRUE | TRUE | TRUE | true | true | FALSE | FALSE | FALSE | true | true | TRUE | TRUE | TRUE | true | true | TRUE | TRUE | TRUE | true | true | true | FALSE | FALSE | FALSE | TRUE | true | true | TRUE | TRUE | TRUE | true | true | TRUE | TRUE | TRUE | true | true | true | true | true | true | TRUE | TRUE | TRUE | TRUE | true | true | false | true | FALSE | FALSE | FALSE
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: ELECTRIC; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; FALSE: HOT_WATER; FALSE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME |  | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | System 7 | System 5 | System 5 | PTHP 1 | System 7 | System 7 | System 11 | System 11 | System Type 3 | System 7 | System 7 | System 12 | System 12 | System 12 | System Type 4 | System 7 | System 7 | System 7 | PTAC 1 | PTAC 1 | PTAC 1 | System 6 | System 7 | System 7 | System 7 | System 5 | System 5 | System 5 | System 5 | System 7 | System 7 | PTAC 1a | PTAC 1a | PTAC 1 | System 7 | System 7 | System 11 | System 11 | System 8 | System 7 | System 7 | System 12 | System 12 | System 10 | System 7 | System 7 | System 7 | PTAC 1 | PTAC 1 | PTAC 1 | System 9 | System 7 | System 7 | System Type 3 | System Type 3 | System 11 | System 7 | System 7 | System 5 | System 5 | System 11 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 12 | System 12 | System 12 | System 12 | System 7 | System 7 | AHU_HW_System1 | System 7 | PTAC 1 | PTAC 1 | PTAC 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | FALSE: CHILLED_WATER; FALSE: CHILLED_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | FALSE: Purchased CHW Loop 1; FALSE: Purchased CHW Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan | id | Fan | Fan 1 | Terminal 1 | id |  |  | FALSE: Fan 1a; FALSE: Fan 1a
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 1 | Zone 1 | fan_configuration |  |  | TRUE: PARALLEL; TRUE: PARALLEL
rmr_template | json_template | JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id |  |  | true: Thermal Zone 2; true: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; TRUE: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; TRUE: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; TRUE: Thermal Zone 2; TRUE: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; false: Thermal Zone 2; true: Thermal Zone 2
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; TRUE: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; true: Required Cooling Schedule 1; false: Required Cooling Schedule 1; true: Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | true: Required Heating Schedule 1; true: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; TRUE: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; true: Required Heating Schedule 1; false: Required Heating Schedule 1; true: Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id |  |  | true: VAV Air Terminal 2; true: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; TRUE: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; true: VAV Air Terminal 2; false: Terminal 2; true: VAV Air Terminal 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | true: true; true: true; TRUE: TRUE; TRUE: TRUE; true: true; true: true; true: true; true: true; true: true; true: true; true: true; TRUE: TRUE; true: true; true: true; true: true; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; TRUE: TRUE; true: true; true: true; true: true; true: true; TRUE: TRUE; true: true; true: true; true: true; true: true; true: true; true: true; true: true; true: true; true: true; TRUE: TRUE; TRUE: TRUE; true: true; true: true; true: true; true: true; true: true; true: true; true: true; true: true; false: false; true: true
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: ELECTRIC; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type |  |  | true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; TRUE: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME; true: VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_system |  |  | true: System 7; true: System 7; TRUE: System 5; TRUE: System 5; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; TRUE: System 6; true: System 7; true: System 7; true: System 7; TRUE: System 5; TRUE: System 5; TRUE: System 5; TRUE: System 5; true: System 7; true: System 7; true: System 7; true: System 7; TRUE: System 8; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; TRUE: System 5; TRUE: System 5; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; true: System 7; false: AHU_HW_System1; true: System 7
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: ELECTRIC; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER; true: HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  | true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan | id | Fan | Fan 2 | Terminal 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | TRUE: PARALLEL; TRUE: PARALLEL
rmr_template | json_template | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System 7 | System 7 | System 5 | System 5 | PTHP 1 | System 7 | System 7 | System 11 | System 11 | System Type 3 | System 7 | System 7 | System 12 | System 12 | System 12 | System Type 4 | System 7 | System 7 | System 7 | PTAC 1 | PTAC 1 | PTAC 1 | System 6 | System 7 | System 7 | System 7 | System 5 | System 5 | System 5 | System 5 | System 7 | System 7 | PTAC 1a | PTAC 1a | PTAC 1 | System 7 | System 7 | System 11 | System 11 | System 8 | System 7 | System 7 | System 12 | System 12 | System 10 | System 7 | System 7 | System 7 | PTAC 1 | PTAC 1 | PTAC 1 | System 9 | System 7 | System 7 | System Type 3 | System Type 3 | System 11 | System 7 | System 7 | System 5 | System 5 | System 11 | System 7 | System 7 | System 7 | System 7 | System 7 | System 7 | System 12 | System 12 | System 12 | System 12 | System 7 | System 7 | AHU_HW_System1 | System 7 | PTAC 1 | PTAC 1 | PTAC 1
rmr_template | json_template | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | FALSE: HP Heating Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Furnace Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: HP Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Furnace Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1; TRUE: Furnace Coil 1; TRUE: Furnace Coil 1; TRUE: Furnace Coil 1; TRUE: Heating Coil 1; TRUE: Heating Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; TRUE: Boiler Coil 1; false: HHW Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1; FALSE: HHW Coil 1
rmr_template | json_template | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | FALSE: HEAT_PUMP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FURNACE; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: HEAT_PUMP; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FURNACE; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP; TRUE: FURNACE; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: ELECTRIC_RESISTANCE; TRUE: ELECTRIC_RESISTANCE; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; false: FLUID_LOOP; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP; FALSE: FLUID_LOOP
rmr_template | json_template | JSON_PATH:heating_system | energy_source_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type |  |  | TRUE: ELECTRICITY; TRUE: NATURAL_GAS
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop |  |  | TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; FALSE: Purchased HW Loop 1; FALSE: Purchased HW Loop 1; FALSE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; false: Purchased HW Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Purchased HW Loop 1
rmr_template | json_template | JSON_PATH:preheat_system | id |  |  | HeatingSystem | Heating System 2 | HVAC 1 | id |  |  | true: Preheat Coil 1; true: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; TRUE: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; TRUE: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; TRUE: Preheat Coil 1; TRUE: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1; true: Preheat Coil 1
rmr_template | json_template | JSON_PATH:preheat_system | heating_system_type |  |  | HeatingSystem | Heating System 2 | HVAC 1 | heating_system_type |  |  | true: FLUID_LOOP; true: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; TRUE: ELECTRIC_RESISTANCE; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; TRUE: ELECTRIC_RESISTANCE; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; TRUE: FLUID_LOOP; TRUE: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP; true: FLUID_LOOP
rmr_template | json_template | JSON_PATH:preheat_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Purchased HW Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 |  |  | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 |  | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 |  | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1
rmr_template | json_template | JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE |  |  | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE |  | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT
rmr_template | json_template | JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
rmr_template | json_template | JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  | Return Fan 1 | Return Fan 1 | Return Fan 1 |  |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  | Return Fan 1
rmr_template | json_template | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1 |  |  |  |  | Boiler 1 | Boiler 1 |  |  |  | Boiler 1 | Boiler 1 |  |  |  | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1 | Boiler 1 | Boiler 1
rmr_template | json_template | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:boilers[0] | draft_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type
rmr_template | json_template | JSON_PATH:boilers[0] | rated_capacity |  |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:boilers[0] | efficiency |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency
rmr_template | json_template | JSON_PATH:boilers[0] | efficiency_metric |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric
rmr_template | json_template | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  |  |  |  | NATURAL_GAS | NATURAL_GAS |  |  |  | NATURAL_GAS | NATURAL_GAS |  |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS
rmr_template | json_template | JSON_PATH:boilers[0] | operation_lower_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit
rmr_template | json_template | JSON_PATH:boilers[0] | operation_upper_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit
rmr_template | json_template | JSON_PATH:boilers[1] | id |  |  | Boiler | Boiler 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:boilers[1] | loop |  |  | Boiler | Boiler 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:boilers[1] | draft_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
rmr_template | json_template | JSON_PATH:boilers[1] | design_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:boilers[1] | energy_source_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:boilers[1] | operation_lower_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit
rmr_template | json_template | JSON_PATH:boilers[1] | operation_upper_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit
rmr_template | json_template | JSON_PATH:boilers[2] | id |  |  | Boiler | Boiler 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:boilers[2] | loop |  |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:boilers[2] | design_capacity |  |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; true: Chiller 1; true: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; TRUE: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; TRUE: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; TRUE: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1; true: Chiller 1
rmr_template | json_template | JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; TRUE: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; TRUE: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; TRUE: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1; true: Chiller Loop 1
rmr_template | json_template | JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
rmr_template | json_template | JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
rmr_template | json_template | JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | HP Cooling Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 |  |  | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 |  | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 |  | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 |  | CHW Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1
rmr_template | json_template | JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP |  |  | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION |  | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP
rmr_template | json_template | JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Chiller Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  |  | Purchased CHW 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  | TRUE: Purchased HW 1; FALSE: Purchased CHW; FALSE: Purchased CHW; FALSE: Purchased HW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; FALSE: Purchased HW 1; FALSE: Purchased HW 1; FALSE: Purchased HW 1; TRUE: Purchased HW; TRUE: Purchased HW; TRUE: Purchased CW 1; TRUE: Purchased HW 1; TRUE: Purchased HW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; TRUE: Purchased CW 1; false: Purchased HW 1; FALSE: Purchased HW 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  | TRUE: Purchased HW Loop 1; FALSE: Purchased CHW Loop 1; FALSE: Purchased CHW Loop 1; FALSE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; FALSE: Purchased HW Loop 1; FALSE: Purchased HW Loop 1; FALSE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Purchased HW Loop 1; TRUE: Purchased HW Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; TRUE: Chilled Water Loop 1; false: Purchased HW Loop 1; FALSE: Purchased HW Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  | TRUE: HOT_WATER; FALSE: CHILLED_WATER; FALSE: CHILLED_WATER; FALSE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; FALSE: HOT_WATER; FALSE: HOT_WATER; FALSE: HOT_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: HOT_WATER; TRUE: HOT_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; TRUE: CHILLED_WATER; false: HOT_WATER; FALSE: HOT_WATER
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | id |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id |  |  | FALSE: Purchased CHW 1
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | loop |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop |  |  | FALSE: Purchased CHW Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | type |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type |  |  | FALSE: CHILLED_WATER
rmr_template | json_template | JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
rmr_template | json_template | JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
rmr_template | json_template | JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
rmr_template | json_template | JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id |  |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  |  |  |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  |  |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  |  |  |  | Boiler Pump 1 | Boiler Pump 1 |  |  | CHW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | HW Pump 1 | Chiller Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1
rmr_template | json_template | JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Chilled Water Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  |  | FIXED_SPEED | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED
rmr_template | json_template | JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
rmr_template | json_template | JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
rmr_template | json_template | JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
rmr_template | json_template | JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
rmr_template | json_template | JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id |  |  | Chiller Pump 1 | Chiller Pump 1 |  |  |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  |  |  |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  |  |  |  | Chiller Pump 1 | Chiller Pump 1 |  |  |  | Chiller Pump 1 | Chiller Pump 1 | CHW Pump 1 | CHW Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | CHW Pump 1 | CHW Pump 1 |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  |  |  |  | Chiller Pump 1 | Chiller Pump 1 |  |  |  | Chiller Pump 1 | Chiller Pump 1 |  |  | Secondary CHW Pump | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | CHW Pump 1 | CHW Pump 1 | CHW Pump 1 | CHW Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  | Chiller Pump 1
rmr_template | json_template | JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  | Secondary CHW Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1
rmr_template | json_template | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  |  | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  |  | FIXED_SPEED | FIXED_SPEED |  |  |  | FIXED_SPEED | FIXED_SPEED |  |  | VARIABLE_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED
rmr_template | json_template | JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W
rmr_template | json_template | JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id |  |  | true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; TRUE: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; TRUE: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump; true: Secondary CHW Pump
rmr_template | json_template | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping |  |  | true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control |  |  | true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED; true: VARIABLE_SPEED
rmr_template | json_template | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Chilled Water Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Chiller Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | HEATING | HEATING | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | COOLING | HEATING | HEATING | HEATING | HEATING | COOLING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id |  |  | TRUE: Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type |  |  | TRUE: COOLING
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | child_loops
rmr_template | json_template | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id |  |  | FALSE: DAC1; FALSE: DAC1; false: DAC 1
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_high_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_high_for_loop_supply_reset_temperature
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_low_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_low_for_loop_supply_reset_temperature
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction |  |  | FALSE: 0.25; FALSE: 0.25
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | flow_control
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | operation
rmr_template | json_template | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Purchased CHW Loop 1 | Purchased CHW Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1 |  |  | Purchased CHW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  | COOLING | COOLING |  |  |  | COOLING | COOLING | COOLING | COOLING |  | COOLING | COOLING | COOLING | COOLING | COOLING |  | COOLING | COOLING | COOLING |  |  |  |  | COOLING | COOLING | COOLING |  |  |  |  | COOLING | COOLING | COOLING | COOLING |  | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING |  | COOLING | COOLING | COOLING |  |  |  |  | COOLING | COOLING |  |  |  | COOLING | COOLING |  |  |  | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING |  | COOLING |  |  | COOLING
rmr_template | json_template | JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id |  |  | true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; TRUE: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1; true: Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type |  |  | true: COOLING; true: COOLING; true: COOLING; true: COOLING; TRUE: COOLING; TRUE: COOLING; true: COOLING; true: COOLING; TRUE: COOLING; TRUE: COOLING; TRUE: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; TRUE: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING; true: COOLING
rmr_transformations | user | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | proposed | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:climate_zone |  |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone |  |  | true: CZ4A; true: CZ4A; TRUE: CZ4A; TRUE: CZ4A; TRUE: CZ4A; TRUE: CZ4A
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id |  |  | true: Space 1; true: Space 1; TRUE: Space 1; TRUE: Space 1; TRUE: Space 1; TRUE: Space 1; true: Space 1; true: Space 1; FALSE: Space 1; FALSE: Space 1; true: Space 1; true: Space 1; TRUE: Space 1; TRUE: Space 1; TRUE: Space 1
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2 | true: 6000; true: 6000; TRUE: 24000; TRUE: 24000; TRUE: 24000; TRUE: 24000; true: 24000; true: 24000; FALSE: 24000; FALSE: 24000; true: 60000; true: 60000; TRUE: 140000; TRUE: 140000; TRUE: 140000
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 1 | Zone 2 | id |  |  | true: Space 2; true: Space 2; true: Space 2; true: Space 2; FALSE: Space 2; FALSE: Space 2; true: Space 2; true: Space 2
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 1 | Zone 2 | floor_area | area | ft2 | true: 6000; true: 6000; true: 6000; true: 6000; FALSE: 6000; FALSE: 6000; true: 40000; true: 40000
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 2 | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:surfaces[0] | id |  |  | Surface | Surface 1 | Zone 1 | id
rmr_transformations | baseline | JSON_PATH:surfaces[0] | adjacent_to |  |  | Surface | Surface 1 | Zone 1 | adjacent_to
rmr_transformations | baseline | JSON_PATH:surfaces[0] | tilt |  |  | Surface | Surface 1 | Zone 1 | tilt
rmr_transformations | baseline | JSON_PATH:surfaces[0] | area |  |  | Surface | Surface 1 | Zone 1 | area | area | ft2
rmr_transformations | baseline | JSON_PATH:surfaces[0] | construction | id |  | Construction | Construction 1 | Surface 1 | id
rmr_transformations | baseline | JSON_PATH:surfaces[0] | construction | u_factor |  | Construction | Construction 1 | Surface 1 | u_factor | thermal_transmittance | Btu/hr-ft2-R
rmr_transformations | baseline | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[0] | draft_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type |  |  | true: NATURAL; true: FORCED; TRUE: NATURAL; TRUE: FORCED
rmr_transformations | baseline | JSON_PATH:boilers[0] | rated_capacity |  |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr | true: 400000; true: 400000; TRUE: 400000; TRUE: 400000; TRUE: 400000; true: 40000; true: 80000; true: 20000; FALSE: 40000; FALSE: 80000; FALSE: 20000; true: 250000; true: 250000; true: 250000; true: 500000; true: 500000; true: 500000; TRUE: 3000000; TRUE: 3000000; TRUE: 3000000
rmr_transformations | baseline | JSON_PATH:boilers[0] | efficiency |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency |  |  | true: 0.8; true: 0.8; true: 0.75; true: 0.75; true: 0.75; true: 0.7; TRUE: 0.8; TRUE: 0.8; TRUE: 0.85
rmr_transformations | baseline | JSON_PATH:boilers[0] | efficiency_metric |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric |  |  | true: ANNUAL_FUEL_UTILIZATION; true: THERMAL; true: ANNUAL_FUEL_UTILIZATION; true: THERMAL; true: ANNUAL_FUEL_UTILIZATION; true: THERMAL; TRUE: COMBUSTION; TRUE: THERMAL; TRUE: COMBUSTION
rmr_transformations | baseline | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | true: ELECTRICITY; true: PROPANE; FALSE: ELECTRICITY
rmr_transformations | baseline | JSON_PATH:boilers[0] | operation_lower_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit | capacity | Btu/hr | true: 0.0; true: 35000; true: 0.0; FALSE: 0.0; FALSE: 35000; FALSE: 0.0
rmr_transformations | baseline | JSON_PATH:boilers[0] | operation_upper_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit | capacity | Btu/hr | true: 40000; true: 115000; true: 40000; FALSE: 40000; FALSE: 115000; FALSE: 40000
rmr_transformations | baseline | JSON_PATH:boilers[1] | id |  |  | Boiler | Boiler 2 | ASHRAE229 1 | id |  |  | true: Boiler 2; TRUE: Boiler 2; TRUE: Boiler 2; true: Boiler 2; true: Boiler 2; true: Boiler 2; FALSE: Boiler 2; FALSE: Boiler 2; FALSE: Boiler 2
rmr_transformations | baseline | JSON_PATH:boilers[1] | loop |  |  | Boiler | Boiler 2 | ASHRAE229 1 | loop |  |  | true: Boiler Loop 1; TRUE: Boiler Loop 1; TRUE: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; true: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1
rmr_transformations | baseline | JSON_PATH:boilers[1] | draft_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
rmr_transformations | baseline | JSON_PATH:boilers[1] | rated_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr | true: 600000; TRUE: 400000; TRUE: 800000; true: 35000; true: 35000; true: 35000; FALSE: 35000; FALSE: 35000; FALSE: 35000
rmr_transformations | baseline | JSON_PATH:boilers[1] | energy_source_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
rmr_transformations | baseline | JSON_PATH:boilers[1] | operation_lower_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit | capacity | Btu/hr | true: 40000; true: 0.0; true: 0.0; FALSE: 40000; FALSE: 0.0; FALSE: 0.0
rmr_transformations | baseline | JSON_PATH:boilers[1] | operation_upper_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit | capacity | Btu/hr | true: 75000; true: 35000; true: 35000; FALSE: 75000; FALSE: 35000; FALSE: 35000
rmr_transformations | baseline | JSON_PATH:boilers[1] | design_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[2] | id |  |  | Boiler | Boiler 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[2] | loop |  |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[2] | rated_capacity |  |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | id |  |  | true: Boiler Loop 1; true: Boiler Loop 1; FALSE: Boiler Loop 1; FALSE: Boiler Loop 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate | power_per_volumetric_flow_rate | W/gpm | true: 19; true: 21; FALSE: 19; FALSE: 21
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | id |  |  | true: Secondary HW Loop 1; TRUE: Secondary HW Loop 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | type |  |  | true: HEATING; TRUE: HEATING
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id |  |  | true: DAC 1; true: DAC 1; TRUE: DAC 1; TRUE: DAC 1; true: DAC 1; true: DAC 1; true: DAC 1; TRUE: DAC 1; TRUE: DAC 1; TRUE: DAC 1; true: DAC 1; true: DAC 1; true: DAC 1; FALSE: DAC 1; FALSE: DAC 1; FALSE: DAC 1; true: DAC 1; true: DAC 1; TRUE: DAC 1; TRUE: DAC 1
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load |  |  | true: true; true: false; TRUE: true; TRUE: false
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F | true: 180; true: 200; true: 180; TRUE: 180; TRUE: 200; TRUE: 180
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F | true: 130; true: 130; true: 150; TRUE: 130; TRUE: 130; TRUE: 150
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control |  | FluidLoopDesignAndControl | Loop 1 | Loop 1 | flow_control |  |  | true: VARIABLE_FLOW; true: VARIABLE_FLOW; true: FIXED_FLOW; FALSE: VARIABLE_FLOW; FALSE: VARIABLE_FLOW; FALSE: FIXED_FLOW
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation |  | FluidLoopDesignAndControl | Loop 1 | Loop 1 | operation |  |  | true: CONTINUOUS; true: INTERMITTENT; true: CONTINUOUS; FALSE: CONTINUOUS; FALSE: INTERMITTENT; FALSE: CONTINUOUS
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | Loop 1 | Loop 1 | minimum_flow_fraction |  |  | true: 0.25; true: 0.3; TRUE: 0.25; TRUE: 0.3
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoopDesignAndControl | Loop 2 | ASHRAE229 1 | id |  |  | TRUE: Boiler Loop 2
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoopDesignAndControl | Loop 2 | ASHRAE229 1 | type |  |  | TRUE: HEATING
rmr_transformations | baseline | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | true: FIXED_SPEED; true: VARIABLE_SPEED; TRUE: VARIABLE_SPEED; TRUE: FIXED_SPEED
rmr_transformations | baseline | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control
rmr_transformations | baseline | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping
rmr_transformations | baseline | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id
rmr_transformations | baseline | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type
rmr_transformations | baseline | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop
rmr_transformations | baseline | JSON_PATH:heating_system | design_capacity | [8 empty] | TRUE: 5000; TRUE: 5000; TRUE: 5000
rmr_transformations | baseline | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id
rmr_transformations | baseline | JSON_PATH:cooling_system | design_sensible_cool_capacity |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | design_sensible_cool_capacity | cooling_capacity | ton | true: 7; true: 7; TRUE: 7; TRUE: 7; TRUE: 7
rmr_transformations | baseline | JSON_PATH:preheat_system | design_capacity |  |  | HeatingSystem | Heating System 1 | HVAC 1 | design_capacity | capacity | Btu/hr | true: 20000; true: 20000
rmr_transformations | baseline | JSON_PATH:fluid_loops[2] | id |  |  | FluidLoopDesignAndControl | Loop 3 | ASHRAE229 1 | id |  |  | true: Boiler Loop 2
rmr_transformations | baseline | JSON_PATH:fluid_loops[2] | type |  |  | FluidLoopDesignAndControl | Loop 3 | ASHRAE229 1 | type |  |  | true: HEATING
rmr_transformations | baseline | JSON_PATH:zones[1] | id | [8 empty] | true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2; FALSE: Thermal Zone 2; FALSE: Thermal Zone 2; true: Thermal Zone 2; true: Thermal Zone 2
rmr_transformations | baseline | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | id
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | heating_source
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | heating_from_loop
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | type
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system

## TCD_Rule_Not_Written
key1 | key2 | key3 | key4 | key5 | key6 | data_group | object_id | parent_id | data_element | unit_type | units | rule-21-1-a | rule-21-1-b | rule-21-1-c | rule-21-2-a | rule-21-2-b | rule-21-8-a | rule-21-8-b | rule-21-14-a | rule-21-14-b | rule-21-15-a | rule-21-15-b
Section | [11 empty] | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Rule | [11 empty] | 1 | 1 | 1 | 2 | 2 | 8 | 8 | 14 | 14 | 15 | 15
Test | [11 empty] | a | b | c | a | b | a | b | a | b | a | b
Notes
test_description | [11 empty] | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler. Expected result: Not Applicable | The project consists of one building segment with one zone. Space conditioning is provided by system type 1a (purchased chilled water). Expected result: Undetermined | The project consists of one building segment with one zone. Space conditioning is provided by system type 1b (purchased hot water). Expected result: Undetermined | The project consists of one building segment with one zone. Space conditioning is provided by system type 5 with boiler. Expected result: Not Applicable | The project consists of one building segment with one zone. Space conditioning is provided by system type 5b (purchased hot water). Expected result: Undetermined | The project consists of one building segment with one zone. Space conditioning is provided by system type 7b with PHW. Expected result: Not Applicable | The project consists of one building segment with one zone. Space conditioning is provided by system type 7 with boiler. Expected result: Undetermined | The project consists of one building segment with one zone. Space conditioning is provided by system type 11.2 with boiler. Expected result: Not Applicable | The project consists of one building segment with one zone. Space conditioning is provided by system type 11.2b with PHW. Expected result: Undetermined | The project consists of one building segment with one zone. Space conditioning is provided by system type 8. Expected result: NOT APPLICABLE | The project consists of one building segment with one zone. Space conditioning is provided by system type 8b with PHW. Expected result: Undetermined
expected_rule_outcome | [11 empty] | not_applicable | undetermined | undetermined | not_applicable | undetermined | not_applicable | undetermined | not_applicable | undetermined | not_applicable | undetermined
standard | rule_id | [10 empty] | 21-1 | 21-1 | 21-1 | 21-2 | 21-2 | 21-8 | 21-8 | 21-14 | 21-14 | 21-15 | 21-15
standard | ruleset_reference | [10 empty] | G3.1.1.3 | G3.1.1.3 | G3.1.1.3 | G3.1.3.5 | G3.1.3.5 | G3.1.3.4 | G3.1.3.4 | G3.1.3.4 | G3.1.3.4 | G3.1.3.5 | G3.1.3.5
standard | rule_description | [10 empty] | For systems using purchased hot water or steam, the heating source shall be modeled as purchased hot water or steam in both the proposed design and baseline building design. If any system in the proposed design uses purchased hot water or steam, all baseline systems with hot water coils shall use the same type of purchased hot water or steam. | For systems using purchased hot water or steam, the heating source shall be modeled as purchased hot water or steam in both the proposed design and baseline building design. If any system in the proposed design uses purchased hot water or steam, all baseline systems with hot water coils shall use the same type of purchased hot water or steam. | For systems using purchased hot water or steam, the heating source shall be modeled as purchased hot water or steam in both the proposed design and baseline building design. If any system in the proposed design uses purchased hot water or steam, all baseline systems with hot water coils shall use the same type of purchased hot water or steam. | For purchased HW/steam in the proposed model, the baseline shall have the same number of pumps as proposed | For purchased HW/steam in the proposed model, the baseline shall have the same number of pumps as proposed | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12),, HWST for the baseline building shall be reset using an outdoor air dry-bulb reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | When the baseline building requires boilers, (for baseline system type = 1,5,7,11 and 12),, HWST for the baseline building shall be reset using an outdoor air dry-bulb reset schedule. 180F at 20F OAT, 150Fat 50F OAT, ramped linerarly between 150F and 180F. | When the baseline building is modeled with a hot water plant, served by purchased HW system, hot water supply temperature reset is not modeled. | When the baseline building is modeled with a hot water plant, served by purchased HW system, hot water supply temperature reset is not modeled. | When the baseline building is modeled with a hot water plant, served by purchased HW system, the hot water pump power shall be 14 W/gpm | When the baseline building is modeled with a hot water plant, served by purchased HW system, the hot water pump power shall be 14 W/gpm
standard | applicable_rmr | [10 empty] | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR | Baseline RMR
standard | rule_assertion | [10 empty] | = | = | = | = | = | = | = | = | = | = | =
standard | comparison_value | [10 empty] | Proposed RMR | Proposed RMR | Proposed RMR | Proposed RMR | Proposed RMR | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value | Expected Value
standard | primary_rule | [10 empty] | No | No | No | No | No | Yes | Yes | No | No | No | No
standard | schema_version | [10 empty] | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23 | 0.0.23
template_lookup | [11 empty] | System_7_VAV_HW_Reheat | System_1a_PTAC | System_1b_PTAC | System_5_PVAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_7b_VAV_HW_Reheat | System_7_VAV_HW_Reheat | System_11.2_VAV_SZ | System_11.2_VAV_SZ | System_3_PSZ_AC_Gas_Furnace | System_7_VAV_HW_Reheat
rmr_template | user
rmr_template | proposed | [10 empty] | true | true | true | true | true
rmr_template | baseline | [10 empty] | true | true | true | true | true | true | true | true | true | true | true
rmr_template | json_template | id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  |  | Calendar | N/A | ASHRAE229 1 | is_leap_year
rmr_template | json_template | ruleset_model_instances[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
rmr_template | json_template | JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
rmr_template | json_template | JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | VAV Air Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | VAV Air Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | true | FALSE | FALSE | TRUE | TRUE | TRUE | true | TRUE | TRUE | TRUE | true
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  | HOT_WATER |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER |  |  |  | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 | PTAC 1 | PTAC 1 | System 5 | System 5 | System 7 | System 7 | System 11 | System 11 | System Type 3 | System 7
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan | id | Fan | Fan 1 | Terminal 1 | id
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 1 | Zone 1 | fan_configuration
rmr_template | json_template | JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id |  |  | Thermal Zone 2 |  |  | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 |  |  |  | Thermal Zone 2
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 |  |  |  | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 |  |  |  | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id |  |  | VAV Air Terminal 2 |  |  | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 |  |  |  | VAV Air Terminal 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  | true |  |  | TRUE | TRUE | TRUE | true |  |  |  | true
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER |  |  |  | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type |  |  | VARIABLE_AIR_VOLUME |  |  | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME |  |  |  | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_system |  |  | System 7 |  |  | System 5 | System 5 | System 7 | System 7 |  |  |  | System 7
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  | HOT_WATER |  |  | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER |  |  |  | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan | id | Fan | Fan 2 | Terminal 2 | id
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration
rmr_template | json_template | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | System 7 | PTAC 1 | PTAC 1 | System 5 | System 5 | System 7 | System 7 | System 11 | System 11 | System Type 3 | System 7
rmr_template | json_template | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  |  | HHW Coil 1 | HHW Coil 1 |  |  |  |  | Boiler Coil 1 | Boiler Coil 1 | Furnace Coil 1
rmr_template | json_template | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  |  | FLUID_LOOP | FLUID_LOOP |  |  |  |  | FLUID_LOOP | FLUID_LOOP | FURNACE
rmr_template | json_template | JSON_PATH:heating_system | energy_source_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop |  |  |  | Boiler Loop 1 | Purchased HW Loop 1 |  |  |  |  | Boiler Loop 1 | Boiler Loop 1
rmr_template | json_template | JSON_PATH:preheat_system | id |  |  | HeatingSystem | Heating System 2 | HVAC 1 | id |  |  | Preheat Coil 1 |  |  | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 |  |  |  | Preheat Coil 1
rmr_template | json_template | JSON_PATH:preheat_system | heating_system_type |  |  | HeatingSystem | Heating System 2 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  |  |  | FLUID_LOOP
rmr_template | json_template | JSON_PATH:preheat_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 |  |  |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1
rmr_template | json_template | JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | VARIABLE_SPEED_DRIVE
rmr_template | json_template | JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
rmr_template | json_template | JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id |  |  | Return Fan 1 |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
rmr_template | json_template | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | Boiler 1 |  | Boiler 1 |  |  | Boiler 1 | Boiler 1 | Boiler 1 |  | Boiler 1
rmr_template | json_template | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:boilers[0] | draft_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type
rmr_template | json_template | JSON_PATH:boilers[0] | rated_capacity |  |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:boilers[0] | efficiency |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency
rmr_template | json_template | JSON_PATH:boilers[0] | efficiency_metric |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric
rmr_template | json_template | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS |  | NATURAL_GAS
rmr_template | json_template | JSON_PATH:boilers[0] | operation_lower_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit
rmr_template | json_template | JSON_PATH:boilers[0] | operation_upper_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit
rmr_template | json_template | JSON_PATH:boilers[1] | id |  |  | Boiler | Boiler 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:boilers[1] | loop |  |  | Boiler | Boiler 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:boilers[1] | draft_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
rmr_template | json_template | JSON_PATH:boilers[1] | design_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:boilers[1] | energy_source_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:boilers[1] | operation_lower_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit
rmr_template | json_template | JSON_PATH:boilers[1] | operation_upper_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit
rmr_template | json_template | JSON_PATH:boilers[2] | id |  |  | Boiler | Boiler 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:boilers[2] | loop |  |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:boilers[2] | design_capacity |  |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_template | json_template | JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id |  |  | Chiller 1 |  |  |  |  | Chiller 1 | Chiller 1 | Chiller 1 | Chiller 1 |  | Chiller 1
rmr_template | json_template | JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop |  |  | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1
rmr_template | json_template | JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
rmr_template | json_template | JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
rmr_template | json_template | JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
rmr_template | json_template | JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
rmr_template | json_template | JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
rmr_template | json_template | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1
rmr_template | json_template | JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP
rmr_template | json_template | JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  | Secondary CHW Loop 1 | Purchased CHW 1 |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id |  |  |  | Purchased CHW 1 | Purchased HW 1 |  | Purchased HW 1 | Purchased HW 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop |  |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Purchased HW Loop 1
rmr_template | json_template | JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type |  |  |  | CHILLED_WATER | HOT_WATER |  | HOT_WATER | HOT_WATER
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | id |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | loop |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:external_fluid_source[1] | type |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
rmr_template | json_template | JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
rmr_template | json_template | JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
rmr_template | json_template | JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
rmr_template | json_template | JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
rmr_template | json_template | JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop
rmr_template | json_template | JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type
rmr_template | json_template | JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id |  |  | Boiler Pump 1 |  |  | Boiler Pump 1 | HW Pump 1 | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 |  | Boiler Pump 1
rmr_template | json_template | JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping |  |  | Boiler Loop 1 |  |  | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED
rmr_template | json_template | JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
rmr_template | json_template | JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
rmr_template | json_template | JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
rmr_template | json_template | JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
rmr_template | json_template | JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id |  |  | Chiller Pump 1 |  |  |  |  | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 | Chiller Pump 1 |  | Chiller Pump 1
rmr_template | json_template | JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping |  |  | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1
rmr_template | json_template | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control |  |  | FIXED_SPEED |  |  |  |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED
rmr_template | json_template | JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W
rmr_template | json_template | JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
rmr_template | json_template | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id |  |  | Secondary CHW Pump |  |  |  |  | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump | Secondary CHW Pump |  | Secondary CHW Pump
rmr_template | json_template | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping |  |  | Secondary CHW Loop 1 |  |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control |  |  | VARIABLE_SPEED |  |  |  |  | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED | VARIABLE_SPEED |  | VARIABLE_SPEED
rmr_template | json_template | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 |  | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
rmr_template | json_template | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type
rmr_template | json_template | JSON_PATH:fluid_loops[0] | child_loops[0] |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | child_loops
rmr_template | json_template | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_high_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_high_for_loop_supply_reset_temperature
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_low_for_loop_supply_reset_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | outdoor_low_for_loop_supply_reset_temperature
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | flow_control
rmr_template | json_template | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | operation
rmr_template | json_template | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  | Chiller Loop 1 | Purchased CHW 1 |  |  |  | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 | Chiller Loop 1 |  | Chiller Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  | COOLING | COOLING |  |  |  | COOLING | COOLING | COOLING | COOLING |  | COOLING
rmr_template | json_template | JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id |  |  | Secondary CHW Loop 1 |  |  |  |  | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
rmr_template | json_template | JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type |  |  | COOLING |  |  |  |  | COOLING | COOLING | COOLING | COOLING |  | COOLING
rmr_transformations | user | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | proposed | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:climate_zone |  |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
rmr_transformations | baseline | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 1 | Zone 2 | id
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 1 | Zone 2 | floor_area | area | ft2
rmr_transformations | baseline | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 2 | occupant_multiplier_schedule
rmr_transformations | baseline | JSON_PATH:surfaces[0] | id |  |  | Surface | Surface 1 | Zone 1 | id
rmr_transformations | baseline | JSON_PATH:surfaces[0] | adjacent_to |  |  | Surface | Surface 1 | Zone 1 | adjacent_to
rmr_transformations | baseline | JSON_PATH:surfaces[0] | tilt |  |  | Surface | Surface 1 | Zone 1 | tilt
rmr_transformations | baseline | JSON_PATH:surfaces[0] | area |  |  | Surface | Surface 1 | Zone 1 | area | area | ft2
rmr_transformations | baseline | JSON_PATH:surfaces[0] | construction | id |  | Construction | Construction 1 | Surface 1 | id
rmr_transformations | baseline | JSON_PATH:surfaces[0] | construction | u_factor |  | Construction | Construction 1 | Surface 1 | u_factor | thermal_transmittance | Btu/hr-ft2-R
rmr_transformations | baseline | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[0] | draft_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type | [9 empty] | NATURAL | FORCED
rmr_transformations | baseline | JSON_PATH:boilers[0] | rated_capacity |  |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[0] | efficiency |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency
rmr_transformations | baseline | JSON_PATH:boilers[0] | efficiency_metric |  |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric
rmr_transformations | baseline | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type
rmr_transformations | baseline | JSON_PATH:boilers[0] | operation_lower_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_lower_limit | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[0] | operation_upper_limit |  |  | Boiler | Boiler 1 | ASHRAE229 1 | operation_upper_limit | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[1] | id |  |  | Boiler | Boiler 2 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[1] | loop |  |  | Boiler | Boiler 2 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[1] | draft_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | draft_type
rmr_transformations | baseline | JSON_PATH:boilers[1] | rated_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[1] | energy_source_type |  |  | Boiler | Boiler 2 | ASHRAE229 1 | energy_source_type
rmr_transformations | baseline | JSON_PATH:boilers[1] | operation_lower_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_lower_limit | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[1] | operation_upper_limit |  |  | Boiler | Boiler 2 | ASHRAE229 1 | operation_upper_limit | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[1] | design_capacity |  |  | Boiler | Boiler 2 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:boilers[2] | id |  |  | Boiler | Boiler 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:boilers[2] | loop |  |  | Boiler | Boiler 3 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:boilers[2] | rated_capacity |  |  | Boiler | Boiler 3 | ASHRAE229 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | loop
rmr_transformations | baseline | JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased HW 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate |  |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | pump_power_per_flow_rate | power_per_volumetric_flow_rate | W/gpm
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoopDesignAndControl | Loop 1 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | is_sized_using_coincident_load
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control |  | FluidLoopDesignAndControl | Loop 1 | Loop 1 | flow_control
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation |  | FluidLoopDesignAndControl | Loop 1 | Loop 1 | operation
rmr_transformations | baseline | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | Loop 1 | Loop 1 | minimum_flow_fraction
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoopDesignAndControl | Loop 2 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoopDesignAndControl | Loop 2 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control
rmr_transformations | baseline | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control
rmr_transformations | baseline | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping
rmr_transformations | baseline | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id
rmr_transformations | baseline | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type
rmr_transformations | baseline | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop
rmr_transformations | baseline | JSON_PATH:heating_system | design_capacity
rmr_transformations | baseline | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id
rmr_transformations | baseline | JSON_PATH:cooling_system | design_sensible_cool_capacity |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | design_sensible_cool_capacity | cooling_capacity | ton
rmr_transformations | baseline | JSON_PATH:preheat_system | design_capacity |  |  | HeatingSystem | Heating System 1 | HVAC 1 | design_capacity | capacity | Btu/hr
rmr_transformations | baseline | JSON_PATH:fluid_loops[2] | id |  |  | FluidLoopDesignAndControl | Loop 3 | ASHRAE229 1 | id
rmr_transformations | baseline | JSON_PATH:fluid_loops[2] | type |  |  | FluidLoopDesignAndControl | Loop 3 | ASHRAE229 1 | type
rmr_transformations | baseline | JSON_PATH:zones[1] | id
rmr_transformations | baseline | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | id
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | heating_source
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | heating_from_loop
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | type
rmr_transformations | baseline | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system

## TCD_KJW_notes
https://github.com/pnnl/ruleset-checking-tool/tree/develop/docs/ruleset_functions/baseline_systems
UPDATE for Jason's comments
Rule tests use 0.0.23
Has
Rules | Is Primary | 1 pass | 1 fail | mimumum of two enumerations | verified against RDS | Generated? | Passed | Description has building description, test description, expected outcome | additional system type tested | non-applicable system tested | tests not working | Notes
21-1 | No | [10 empty] | keep non-primary because of central plant, write RDS
21-2 | No | [10 empty] | keep non-primary because of central plant, write RDS
21-3 | Yes | yes | yes | yes | yes |  |  | yes | 5 | 2
21-4 | Yes | yes | yes | yes | yes |  |  | yes | 11.2 | 3
21-5 | Yes | yes | yes | yes | yes |  |  | yes | 12 | 4 | c,d,e | added an additional fail test for large building with only one boiler
21-6 | Yes | yes | yes | yes | yes |  |  | yes | 1 | 6
21-7 | Yes | yes | yes | yes | yes |  |  | yes | 5 | 5b |  | added enumeration to test both incorrect setpoints (one test for 200F/130F & another for 180F/150F) general question - the rule logic is written for IP units, but the schema specifies SI, does Weili's team do the unit conversion?
21-8 | Yes | [10 empty] | CHANGE TO PRIMARY, WRITE RDS
21-9 | Yes | yes | yes | yes | yes |  |  | yes | 1a | 1b | c - sys type is 1b, is not identified as any specific system type
21-10 | Yes | yes | yes | yes | yes |  |  | yes | 11.2a | 8 | c - no system type is identified, should be 11.2 | should this rule apply to 11.1b also???
21-11 | Yes | yes | yes | yes | yes |  |  | yes | 12a | 10
21-12 | Yes | yes | yes | yes | yes |  |  | yes | 1b | 9 | def | added enumeration to test both flow control and operation
21-13 | Yes | yes | yes | yes | yes |  |  | yes | 3b | 11.1a
21-14 | No | [10 empty] | keep non-primary because of central plant, write RDS
21-15 | No | [10 empty] | keep non-primary because of central plant, write RDS
21-16 | Yes | yes | yes | yes | yes |  |  | yes | 5b | 11.1 | c
21-17 | Yes | yes | yes | yes | yes |  |  | yes | 12a | 12b |  | added enumerations to test AFUE and efficiency metric separately
21-18 | Yes | yes | yes | yes | yes |  |  | yes | 1 | 12c |  | added enumeration to test undetermined
other notes
rule "passes" if there is any issue in processing & expected output is fail
0 issue in spreadsheet
21-4-c - this is being identified by the program as system type 3, not 11.2, causing test to fail
airside_hvac_master notes
some system types did not have hot water loop specified even though it was referenced (formula added in rows 103 & 104)
System_5b_PVAV_HW_Reheat - terminal[1]:heating_from_loop was wrong, corrected in cell V33
system_3c - cells S110 and 111 - should these be in the child loop section?
Systems 1b & 1c purchased heating and cooling loops weren't identified with an ID
System 11.2a - changed fan control to VARIABLE_SPEED_DRIVE
for hvac systems - how to create with more than one zone / floor?

## Lookups
test_outcome_types | true/false | yes/no | applicable_rmr | rule_assertions | comparison_rmr
pass | true | Yes | User RMR | = | Expected Value
fail | false | No | Proposed RMR | <= | User RMR
manual_check |  |  | Baseline RMR | >= | Proposed RMR
caution |  |  |  |  | Baseline RMR
undetermined
not_applicable

## All_SYSTEM_TYPES
| lookup | key1 | key2 | key3 | key4 | data_group | object_id | parent_id | data_element | unit_type | units | System_1_PTAC | System_1a_PTAC | System_1b_PTAC | System_1c_PTAC | System_2_PTHP | System_3_PSZ_AC_Gas_Furnace | System_3a_PSZ_AC_Gas_Furnace | System_3b_PSZ_AC_Gas_Furnace | System_3c_PSZ_AC_Gas_Furnace | System_4_PSZ_HP | System_5_PVAV_HW_Reheat | System_5b_PVAV_HW_Reheat | System_6_PVAV_Elec_Reheat | System_6b_PVAV_Elec_Reheat | System_7_VAV_HW_Reheat | System_7a_VAV_HW_Reheat | System_7b_VAV_HW_Reheat | System_7c_VAV_HW_Reheat | System_8_PFP_Reheat | System_8a_PFP_Reheat | System_8b_PFP_Reheat | System_8c_PFP_Reheat | System_9_Warm_Air_Furnace_Gas | System_9b_Warm_Air_Furnace_Gas | System_10_Warm_Air_Furnace_Elec | System_11.1_VAV_SZ | System_11.1a_VAV_SZ | System_11.1b_VAV_SZ | System_11.1c_VAV_SZ | System_11.2_VAV_SZ | System_11.2a_VAV_SZ | System 12_CAV_SZ_HW | System 12a_CAV_SZ_HW | System 12b_CAV_SZ_HW | System 12c_CAV_SZ_HW | System 13_CAV_SZ_ER | System 13a_CAV_SZ_ER
id::: | id::: | id |  |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1 | ASHRAE229 1
weather:climate_zone:: | weather:climate_zone:: | weather | climate_zone |  |  | ASHRAE229 | ASHRAE229 1 | weather | climate_zone
ruleset_model_instances[0]:id:: | ruleset_model_instances[0]:id:: | ruleset_model_instances[0] | id |  |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1 | RMD 1
JSON_PATH:buildings[0]:id:: | JSON_PATH:buildings[0]:id:: | JSON_PATH:buildings[0] | id |  |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1 | Building 1
JSON_PATH:buildings[0]:building_open_schedule:: | JSON_PATH:buildings[0]:building_open_schedule:: | JSON_PATH:buildings[0] | building_open_schedule |  |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1 | Required Building Schedule 1
JSON_PATH: building_segments[0]:id:: | JSON_PATH: building_segments[0]:id:: | JSON_PATH: building_segments[0] | id |  |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1 | Building Segment 1
JSON_PATH:zones[0]:id:: | JSON_PATH:zones[0]:id:: | JSON_PATH:zones[0] | id |  |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1 | Thermal Zone 1
JSON_PATH:zones[0]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[0]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[0]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[0]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[0]:spaces[0]:id: | JSON_PATH:zones[0]:spaces[0]:id: | JSON_PATH:zones[0] | spaces[0] | id |  | Space | Space 1 | Zone 1 | id
JSON_PATH:zones[0]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[0]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 1 | Zone 1 | occupant_multiplier_schedule
JSON_PATH:zones[0]:spaces[0]:floor_area: | JSON_PATH:zones[0]:spaces[0]:floor_area: | JSON_PATH:zones[0] | spaces[0] | floor_area |  | Space | Space 1 | Zone 1 | floor_area | area | ft2
JSON_PATH:zones[0]:terminals[0]:id: | JSON_PATH:zones[0]:terminals[0]:id: | JSON_PATH:zones[0] | terminals[0] | id |  | Air Terminal | Terminal 1 | Zone 1 | id |  |  | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTAC Terminal 1 | PTHP Terminal 1 | Air Terminal | Air Terminal | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | Air Terminal | Air Terminal | Air Terminal | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | VAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1 | CAV Air Terminal 1
JSON_PATH:zones[0]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[0]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
JSON_PATH:zones[0]:terminals[0]:type: | JSON_PATH:zones[0]:terminals[0]:type: | JSON_PATH:zones[0] | terminals[0] | type |  | Air Terminal | Terminal 1 | Zone 1 | type |  |  | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME | CONSTANT_AIR_VOLUME
JSON_PATH:zones[0]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[0]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_systems |  |  | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTHP 1 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 4 | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | System 9 | System 9B | System 10 | System 11 | System 11 | System 11 | System 11 | System 11 | System 11 | System 12 | System 12 | System 12 | System 12 | System 13 | System 13
JSON_PATH:zones[0]:terminals[0]:heating_source: | JSON_PATH:zones[0]:terminals[0]:heating_source: | JSON_PATH:zones[0] | terminals[0] | heating_source |  | Air Terminal | Terminal 1 | Zone 1 | heating_source | [12 empty] | HOT_WATER | HOT_WATER | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER |  | HOT_WATER
JSON_PATH:zones[0]:terminals[0]:heating_from_loop: | JSON_PATH:zones[0]:terminals[0]:heating_from_loop: | JSON_PATH:zones[0] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop | [12 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1
#N/A | JSON_PATH:zones[0]:terminals[0]:fan[0]:id | JSON_PATH:zones[0] | terminals[0] | fan[0] | id | Air Terminal | Terminal 1 | Zone 1 | fan | [25 empty] | fan 1 | Terminal Fan 1
JSON_PATH:zones[0]:terminals[0]:fan_configuration: | JSON_PATH:zones[0]:terminals[0]:fan_configuration: | JSON_PATH:zones[0] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 1 | Zone 1 | fan_configuration | [14 empty] | PARALLEL | PARALLEL |  |  |  |  | PARALLEL | PARALLEL | PARALLEL | PARALLEL
JSON_PATH:zones[1]:id:: | JSON_PATH:zones[1]:id:: | JSON_PATH:zones[1] | id |  |  | Zone | Zone 2 | Building Segment 1 | id | [12 empty] | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2 | Thermal Zone 2
JSON_PATH:zones[1]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[1]:thermostat_cooling_setpoint_schedule:: | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule | [12 empty] | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1 | Required Cooling Schedule 1
JSON_PATH:zones[1]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[1]:thermostat_heating_setpoint_schedule:: | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule | [12 empty] | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1 | Required Heating Schedule 1
JSON_PATH:zones[1]:spaces[0]:id: | JSON_PATH:zones[1]:spaces[0]:id: | JSON_PATH:zones[1] | spaces[0] | id |  | Space | Space 2 | Zone 2 | id
JSON_PATH:zones[1]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[1]:spaces[0]:occupant_multiplier_schedule: | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule |  | Space | Space 2 | Zone 2 | occupant_multiplier_schedule
JSON_PATH:zones[1]:spaces[0]:floor_area: | JSON_PATH:zones[1]:spaces[0]:floor_area: | JSON_PATH:zones[1] | spaces[0] | floor_area |  | Space | Space 2 | Zone 2 | floor_area | area | ft2
JSON_PATH:zones[1]:terminals[0]:id: | JSON_PATH:zones[1]:terminals[0]:id: | JSON_PATH:zones[1] | terminals[0] | id |  | Air Terminal | Terminal 2 | Zone 2 | id | [12 empty] | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2 | VAV Air Terminal 2
JSON_PATH:zones[1]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[1]:terminals[0]:is_supply_ducted: | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration | [12 empty] | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
JSON_PATH:zones[1]:terminals[0]:type: | JSON_PATH:zones[1]:terminals[0]:type: | JSON_PATH:zones[1] | terminals[0] | type |  | Air Terminal | Terminal 2 | Zone 2 | type | [12 empty] | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME | VARIABLE_AIR_VOLUME
JSON_PATH:zones[1]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[1]:terminals[0]:served_by_heating_ventilating_air_conditioning_system: | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system |  | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_systems | [12 empty] | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8
JSON_PATH:zones[1]:terminals[0]:heating_source: | JSON_PATH:zones[1]:terminals[0]:heating_source: | JSON_PATH:zones[1] | terminals[0] | heating_source |  | Air Terminal | Terminal 2 | Zone 2 | heating_source | [12 empty] | HOT_WATER | HOT_WATER | ELECTRIC | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER | HOT_WATER
JSON_PATH:zones[1]:terminals[0]:heating_from_loop: | JSON_PATH:zones[1]:terminals[0]:heating_from_loop: | JSON_PATH:zones[1] | terminals[0] | heating_from_loop |  | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop | [12 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:zones[1]:terminals[0]:fan:id | JSON_PATH:zones[1]:terminals[0]:fan:id | JSON_PATH:zones[1] | terminals[0] | fan | id | Air Terminal | Terminal 2 | Zone 2 | fan
JSON_PATH:zones[1]:terminals[0]:fan_configuration: | JSON_PATH:zones[1]:terminals[0]:fan_configuration: | JSON_PATH:zones[1] | terminals[0] | fan_configuration |  | Air Terminal | Terminal 2 | Zone 2 | fan_configuration | [14 empty] | PARALLEL | PARALLEL |  |  |  |  | PARALLEL | PARALLEL | PARALLEL | PARALLEL
JSON_PATH:heating_ventilating_air_conditioning_systems[0]:id:: | JSON_PATH:heating_ventilating_air_conditioning_systems[0]:id:: | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | PTAC 1 | PTAC 1 | PTAC 1 | PTAC 1 | PTHP 1 | System Type 3 | System Type 3 | System Type 3 | System Type 3 | System Type 4 | System 5 | System 5 | System 6 | System 6 | System 7 | System 7 | System 7 | System 7 | System 8 | System 8 | System 8 | System 8 | System 9 | System 9B | System 10 | System 11 | System 11 | System 11 | System 11 | System 11 | System 11 | System 12 | System 12 | System 12 | System 12 | System 13 | System 13
JSON_PATH:cooling_system:id:: | JSON_PATH:cooling_system:id:: | JSON_PATH:cooling_system | id |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | id |  |  | DX Coil 1 | CHW Coil 1 | DX Coil 1 | CHW Coil 1 | HP Cooling Coil 1 | DX Coil 1 | Cooling Coil 1 | DX Coil 1 | Cooling Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | DX Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 |  |  |  | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1 | CHW Coil 1
JSON_PATH:cooling_system:cooling_system_type:: | JSON_PATH:cooling_system:cooling_system_type:: | JSON_PATH:cooling_system | cooling_system_type |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | cooling_system_type |  |  | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | FLUID_LOOP | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | DIRECT_EXPANSION | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP |  |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
JSON_PATH:cooling_system:chilled_water_loop:: | JSON_PATH:cooling_system:chilled_water_loop:: | JSON_PATH:cooling_system | chilled_water_loop |  |  | CoolingSystem | Cooling System 1 | HVAC 1 | chilled_water_loop |  |  |  | Purchased CHW 1 |  | Purchased CHW 1 |  |  | Purchased CHW Loop 1 |  | Purchased CHW Loop 1 | [5 empty] | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 |  |  |  | Secondary CHW Loop 1 | Chiller Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Secondary CHW Loop 1 | Chilled Water Loop 1
JSON_PATH:heating_system:id:: | JSON_PATH:heating_system:id:: | JSON_PATH:heating_system | id |  |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | HHW Coil 1 | HP Heating Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | Furnace Coil 1 | HP Coil 1 | [12 empty] | Furnace Coil 1 |  | Furnace Coil 1 | Heating Coil 1 | Heating Coil 1 | HHW Coil 1 | HHW Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Boiler Coil 1 | Boiler Coil 1 | HHW Coil 1 | HHW Coil 1 | Heating Coil 1 | Heating Coil 1
JSON_PATH:heating_system:heating_system_type:: | JSON_PATH:heating_system:heating_system_type:: | JSON_PATH:heating_system | heating_system_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | HEAT_PUMP | FURNACE | FURNACE | FLUID_LOOP | FLUID_LOOP | HEAT_PUMP | [12 empty] | FURNACE |  | FURNACE | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | ELECTRIC_RESISTANCE
JSON_PATH:heating_system:energy_source_type:: | JSON_PATH:heating_system:energy_source_type:: | JSON_PATH:heating_system | energy_source_type |  |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type | [24 empty] | NATURAL_GAS |  | ELECTRICITY
JSON_PATH:heating_system:hot_water_loop:: | JSON_PATH:heating_system:hot_water_loop:: | JSON_PATH:heating_system | hot_water_loop |  |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  |  | Purchased HW Loop 1 | Purchased HW Loop 1 | [18 empty] | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:preheat_system:id:: | JSON_PATH:preheat_system:id:: | JSON_PATH:preheat_system | id |  |  | PreheatSystem | Heating System 1 | HVAC 1 | id | [12 empty] | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1 | Preheat Coil 1
JSON_PATH:preheat_system:heating_system_type:: | JSON_PATH:preheat_system:heating_system_type:: | JSON_PATH:preheat_system | heating_system_type |  |  | PreheatSystem | Heating System 1 | HVAC 1 | heating_system_type | [12 empty] | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP | ELECTRIC_RESISTANCE | FLUID_LOOP | FLUID_LOOP | FLUID_LOOP
JSON_PATH:preheat_system:hot_water_loop:: | JSON_PATH:preheat_system:hot_water_loop:: | JSON_PATH:preheat_system | hot_water_loop |  |  | PreheatSystem | Heating System 2 | HVAC 1 | hot_water_loop | [12 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1
JSON_PATH:fan_system:id:: | JSON_PATH:fan_system:id:: | JSON_PATH:fan_system | id |  |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 |  |  | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | VAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1 | CAV Fan System 1
JSON_PATH:fan_system:fan_control:: | JSON_PATH:fan_system:fan_control:: | JSON_PATH:fan_system | fan_control |  |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT |  |  | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | VARIABLE_SPEED_DRIVE | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT | CONSTANT
JSON_PATH:fan_system:supply_fans[0]:id: | JSON_PATH:fan_system:supply_fans[0]:id: | JSON_PATH:fan_system | supply_fans[0] | id |  | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 |  |  | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1 | Supply Fan 1
JSON_PATH:fan_system:return_fans[0]:id: | JSON_PATH:fan_system:return_fans[0]:id: | JSON_PATH:fan_system | return_fans[0] | id |  | Fan | Return Fan 1 | HVAC 1 | id | [7 empty] | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 |  |  | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1 | Return Fan 1
JSON_PATH:boilers[0]:id:: | JSON_PATH:boilers[0]:id:: | JSON_PATH:boilers[0] | id |  |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | Boiler 1 | [8 empty] | Boiler 1 |  |  |  | Boiler 1 | Boiler 1 |  |  | Boiler 1 | Boiler 1 | [9 empty] | Boiler 1 | Boiler 1 | Boiler 1 | Boiler 1
JSON_PATH:boilers[0]:loop:: | JSON_PATH:boilers[0]:loop:: | JSON_PATH:boilers[0] | loop |  |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 | Boiler Loop 1 | [8 empty] | Boiler Loop 1 |  |  |  | Boiler Loop 1 | Boiler Loop 1 |  |  | Boiler Loop 1 | Boiler Loop 1 | [9 empty] | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1
JSON_PATH:boilers[0]:energy_source_type:: | JSON_PATH:boilers[0]:energy_source_type:: | JSON_PATH:boilers[0] | energy_source_type |  |  | Boiler | Boiler 1 | ASHRAE229 1 | energy_source_type |  |  | NATURAL_GAS | NATURAL_GAS | [8 empty] | NATURAL_GAS |  |  |  | NATURAL_GAS | NATURAL_GAS |  |  | NATURAL_GAS | NATURAL_GAS | [9 empty] | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS | NATURAL_GAS
JSON_PATH:chillers[0]:id:: | JSON_PATH:chillers[0]:id:: | JSON_PATH:chillers[0] | id |  |  | Chiller | Chiller 1 | ASHRAE229 1 | id | [16 empty] | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  |  |  |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1 |  | Chiller 1
JSON_PATH:chillers[0]:cooling_loop:: | JSON_PATH:chillers[0]:cooling_loop:: | JSON_PATH:chillers[0] | cooling_loop |  |  | Chiller | Chiller 1 | ASHRAE229 1 | cooling_loop | [16 empty] | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  |  |  |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1 |  | Chiller Loop 1
JSON_PATH:chillers[0]:design_capacity:: | JSON_PATH:chillers[0]:design_capacity:: | JSON_PATH:chillers[0] | design_capacity |  |  | Chiller | Chiller 1 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[0]:energy_source_type:: | JSON_PATH:chillers[0]:energy_source_type:: | JSON_PATH:chillers[0] | energy_source_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | energy_source_type
JSON_PATH:chillers[0]:full_load_efficiency:: | JSON_PATH:chillers[0]:full_load_efficiency:: | JSON_PATH:chillers[0] | full_load_efficiency |  |  | Chiller | Chiller 1 | ASHRAE229 1 | full_load_efficiency | cooling_efficiency | kW/ton
JSON_PATH:chillers[0]:compressor_type:: | JSON_PATH:chillers[0]:compressor_type:: | JSON_PATH:chillers[0] | compressor_type |  |  | Chiller | Chiller 1 | ASHRAE229 1 | compressor_type
JSON_PATH:chillers[1]:id:: | JSON_PATH:chillers[1]:id:: | JSON_PATH:chillers[1] | id |  |  | Chiller | Chiller 2 | ASHRAE229 1 | id
JSON_PATH:chillers[1]:cooling_loop:: | JSON_PATH:chillers[1]:cooling_loop:: | JSON_PATH:chillers[1] | cooling_loop |  |  | Chiller | Chiller 2 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[1]:design_capacity:: | JSON_PATH:chillers[1]:design_capacity:: | JSON_PATH:chillers[1] | design_capacity |  |  | Chiller | Chiller 2 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[2]:id:: | JSON_PATH:chillers[2]:id:: | JSON_PATH:chillers[2] | id |  |  | Chiller | Chiller 3 | ASHRAE229 1 | id
JSON_PATH:chillers[2]:cooling_loop:: | JSON_PATH:chillers[2]:cooling_loop:: | JSON_PATH:chillers[2] | cooling_loop |  |  | Chiller | Chiller 3 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[2]:design_capacity:: | JSON_PATH:chillers[2]:design_capacity:: | JSON_PATH:chillers[2] | design_capacity |  |  | Chiller | Chiller 3 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:chillers[3]:id:: | JSON_PATH:chillers[3]:id:: | JSON_PATH:chillers[3] | id |  |  | Chiller | Chiller 4 | ASHRAE229 1 | id
JSON_PATH:chillers[3]:cooling_loop:: | JSON_PATH:chillers[3]:cooling_loop:: | JSON_PATH:chillers[3] | cooling_loop |  |  | Chiller | Chiller 4 | ASHRAE229 1 | cooling_loop
JSON_PATH:chillers[3]:design_capacity:: | JSON_PATH:chillers[3]:design_capacity:: | JSON_PATH:chillers[3] | design_capacity |  |  | Chiller | Chiller 4 | ASHRAE229 1 | design_capacity | cooling_capacity | ton
JSON_PATH:external_fluid_source[0]:id:: | JSON_PATH:external_fluid_source[0]:id:: | JSON_PATH:external_fluid_source[0] | id |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | id |  |  |  | Purchased CHW 1 | Purchased HW 1 | Purchased HW 1 |  |  | Purchased CHW | Purchased HW | Purchased CHW |  |  | Purchased HW 1 |  | Purchased HW 1 |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased HW 1 |  |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased CW 1 |  | Purchased CW 1 | Purchased HW 1 | Purchased HW 1 |  | Purchased CW 1
JSON_PATH:external_fluid_source[0]:loop:: | JSON_PATH:external_fluid_source[0]:loop:: | JSON_PATH:external_fluid_source[0] | loop |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | loop |  |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased CHW Loop 1 |  |  | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Chilled Water Loop 1 |  | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Chilled Water Loop 1
JSON_PATH:external_fluid_source[0]:type:: | JSON_PATH:external_fluid_source[0]:type:: | JSON_PATH:external_fluid_source[0] | type |  |  | ExternalFluidSource | Purchased Loop 1 | ASHRAE229 1 | type |  |  |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  |  | CHILLED_WATER | HOT_WATER | CHILLED_WATER |  |  | HOT_WATER |  | HOT_WATER |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | HOT_WATER |  |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | CHILLED_WATER |  | CHILLED_WATER | HOT_WATER | HOT_WATER |  | CHILLED_WATER
JSON_PATH:external_fluid_source[1]:id:: | JSON_PATH:external_fluid_source[1]:id:: | JSON_PATH:external_fluid_source[1] | id |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | id | [5 empty] | Purchased CHW 1 |  |  |  |  | Purchased HW | [8 empty] | Purchased CW 1 |  |  |  | Purchased CW 1 | [6 empty] | Purchased CW 1 | [5 empty] | Purchased CW 1
JSON_PATH:external_fluid_source[1]:loop:: | JSON_PATH:external_fluid_source[1]:loop:: | JSON_PATH:external_fluid_source[1] | loop |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | loop | [5 empty] | Purchased CHW Loop 1 |  |  |  |  | Purchased HW Loop 1 | [8 empty] | Chilled Water Loop 1 |  |  |  | Chilled Water Loop 1 | [6 empty] | Chilled Water Loop 1 | [5 empty] | Chilled Water Loop 1
JSON_PATH:external_fluid_source[1]:type:: | JSON_PATH:external_fluid_source[1]:type:: | JSON_PATH:external_fluid_source[1] | type |  |  | ExternalFluidSource | Purchased Loop 2 | ASHRAE229 1 | type | [5 empty] | CHILLED_WATER |  |  |  |  | HOT_WATER | [8 empty] | CHILLED_WATER |  |  |  | CHILLED_WATER | [6 empty] | CHILLED_WATER | [5 empty] | CHILLED_WATER
JSON_PATH:heat_rejections[0]:id:: | JSON_PATH:heat_rejections[0]:id:: | JSON_PATH:heat_rejections[0] | id |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | id
JSON_PATH:heat_rejections[0]:loop:: | JSON_PATH:heat_rejections[0]:loop:: | JSON_PATH:heat_rejections[0] | loop |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | loop
JSON_PATH:heat_rejections[0]:type:: | JSON_PATH:heat_rejections[0]:type:: | JSON_PATH:heat_rejections[0] | type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | type
JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
JSON_PATH:heat_rejections[0]:design_water_flowrate:: | JSON_PATH:heat_rejections[0]:design_water_flowrate:: | JSON_PATH:heat_rejections[0] | design_water_flowrate |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_water_flowrate | fluid_flow_rate | gallon/min
JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0]:design_wetbulb_temperature:: | JSON_PATH:heat_rejections[0] | design_wetbulb_temperature |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | design_wetbulb_temperature | temperature | F
JSON_PATH:heat_rejections[0]:fan_speed_control:: | JSON_PATH:heat_rejections[0]:fan_speed_control:: | JSON_PATH:heat_rejections[0] | fan_speed_control |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | fan_speed_control
JSON_PATH:heat_rejections[0]:range:: | JSON_PATH:heat_rejections[0]:range:: | JSON_PATH:heat_rejections[0] | range |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | range | temperature_difference | R
JSON_PATH:heat_rejections[0]:reset_type:: | JSON_PATH:heat_rejections[0]:reset_type:: | JSON_PATH:heat_rejections[0] | reset_type |  |  | HeatRejection | Cooling Tower 1 | ASHRAE229 1 | reset_type
JSON_PATH:heat_rejections[1]:id:: | JSON_PATH:heat_rejections[1]:id:: | JSON_PATH:heat_rejections[1] | id |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | id
JSON_PATH:heat_rejections[1]:loop:: | JSON_PATH:heat_rejections[1]:loop:: | JSON_PATH:heat_rejections[1] | loop |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | loop
JSON_PATH:heat_rejections[1]:type:: | JSON_PATH:heat_rejections[1]:type:: | JSON_PATH:heat_rejections[1] | type |  |  | HeatRejection | Cooling Tower 2 | ASHRAE229 1 | type
JSON_PATH:pumps[0]:id:: | JSON_PATH:pumps[0]:id:: | JSON_PATH:pumps[0] | id |  |  | Pump | Pump 1 | ASHRAE229 1 | id | [12 empty] | Boiler Pump 1 | HW Pump 1 |  | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | HW Pump 1 |  | HW Pump 1 |  | Chiller Pump 1 | CHW Pump 1 | HW Pump 1 | HW Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | Boiler Pump 1 | HW Pump 1 | HW Pump 1 | Chiller Pump 1 | CHW Pump 1
JSON_PATH:pumps[0]:loop_or_piping:: | JSON_PATH:pumps[0]:loop_or_piping:: | JSON_PATH:pumps[0] | loop_or_piping |  |  | Pump | Pump 1 | ASHRAE229 1 | loop_or_piping | [12 empty] | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Chiller Loop 1 | Chilled Water Loop 1
JSON_PATH:pumps[0]:speed_control:: | JSON_PATH:pumps[0]:speed_control:: | JSON_PATH:pumps[0] | speed_control |  |  | Pump | Pump 1 | ASHRAE229 1 | speed_control | [12 empty] | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  | FIXED_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED
JSON_PATH:pumps[0]:design_electric_power:: | JSON_PATH:pumps[0]:design_electric_power:: | JSON_PATH:pumps[0] | design_electric_power |  |  | Pump | Pump 1 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[0]:design_flow:: | JSON_PATH:pumps[0]:design_flow:: | JSON_PATH:pumps[0] | design_flow |  |  | Pump | Pump 1 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[0]:design_head:: | JSON_PATH:pumps[0]:design_head:: | JSON_PATH:pumps[0] | design_head |  |  | Pump | Pump 1 | ASHRAE229 1 | design_head | pump_head | ft
JSON_PATH:pumps[0]:motor_efficiency:: | JSON_PATH:pumps[0]:motor_efficiency:: | JSON_PATH:pumps[0] | motor_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | motor_efficiency
JSON_PATH:pumps[0]:impeller_efficiency:: | JSON_PATH:pumps[0]:impeller_efficiency:: | JSON_PATH:pumps[0] | impeller_efficiency |  |  | Pump | Pump 1 | ASHRAE229 1 | impeller_efficiency
JSON_PATH:pumps[1]:id:: | JSON_PATH:pumps[1]:id:: | JSON_PATH:pumps[1] | id |  |  | Pump | Pump 2 | ASHRAE229 1 | id | [16 empty] | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 |  |  |  | Secondary CHW Pump |  | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Chiller Pump 1 | CHW Pump 1 | Secondary CHW Pump
JSON_PATH:pumps[1]:loop_or_piping:: | JSON_PATH:pumps[1]:loop_or_piping:: | JSON_PATH:pumps[1] | loop_or_piping |  |  | Pump | Pump 2 | ASHRAE229 1 | loop_or_piping | [16 empty] | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 |  |  |  | Secondary CHW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Secondary CHW Loop 1
JSON_PATH:pumps[1]:speed_control:: | JSON_PATH:pumps[1]:speed_control:: | JSON_PATH:pumps[1] | speed_control |  |  | Pump | Pump 2 | ASHRAE229 1 | speed_control | [16 empty] | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED |  |  |  | VARIABLE_SPEED |  | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | FIXED_SPEED | VARIABLE_SPEED
JSON_PATH:pumps[1]:design_electric_power:: | JSON_PATH:pumps[1]:design_electric_power:: | JSON_PATH:pumps[1] | design_electric_power |  |  | Pump | Pump 2 | ASHRAE229 1 | design_electric_power | electric_power | W
JSON_PATH:pumps[1]:design_flow:: | JSON_PATH:pumps[1]:design_flow:: | JSON_PATH:pumps[1] | design_flow |  |  | Pump | Pump 2 | ASHRAE229 1 | design_flow | fluid_flow_rate | gallon/min
JSON_PATH:pumps[2]:id:: | JSON_PATH:pumps[2]:id:: | JSON_PATH:pumps[2] | id |  |  | Pump | Pump 3 | ASHRAE229 1 | id | [16 empty] | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump | [6 empty] | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump |  | Secondary CHW Pump
JSON_PATH:pumps[2]:loop_or_piping:: | JSON_PATH:pumps[2]:loop_or_piping:: | JSON_PATH:pumps[2] | loop_or_piping |  |  | Pump | Pump 3 | ASHRAE229 1 | loop_or_piping | [16 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [6 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
JSON_PATH:pumps[2]:speed_control:: | JSON_PATH:pumps[2]:speed_control:: | JSON_PATH:pumps[2] | speed_control |  |  | Pump | Pump 3 | ASHRAE229 1 | speed_control | [16 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED | [6 empty] | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED |  | VARIABLE_SPEED
JSON_PATH:fluid_loops[0]:id:: | JSON_PATH:fluid_loops[0]:id:: | JSON_PATH:fluid_loops[0] | id |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | id |  |  | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  |  | Purchased CHW Loop 1 | Purchased HW Loop 1 | Purchased CHW Loop 1 |  | Boiler Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 |  | Purchased HW Loop 1 |  | Chiller Loop 1 | Chilled Water Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Boiler Loop 1 | Purchased HW Loop 1 | Purchased HW Loop 1 | Chiller Loop 1 | Chilled Water Loop 1
JSON_PATH:fluid_loops[0]:type:: | JSON_PATH:fluid_loops[0]:type:: | JSON_PATH:fluid_loops[0] | type |  |  | FluidLoop | Loop 1 | ASHRAE229 1 | type |  |  | HEATING | HEATING | HEATING | HEATING |  |  | COOLING | HEATING | COOLING |  | HEATING | HEATING |  | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING |  | HEATING |  | COOLING | COOLING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | HEATING | COOLING | COOLING
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:id: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:id: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | id |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | id
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_supply_temperature: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_supply_temperature: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_supply_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_supply_temperature | temperature | F
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_return_temperature: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:design_return_temperature: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | design_return_temperature |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | design_return_temperature | temperature | F
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:temperature_reset_type: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:temperature_reset_type: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | temperature_reset_type |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | temperature_reset_type
JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:minimum_flow_fraction: | JSON_PATH:fluid_loops[0]:cooling_or_condensing_design_and_control:minimum_flow_fraction: | JSON_PATH:fluid_loops[0] | cooling_or_condensing_design_and_control | minimum_flow_fraction |  | FluidLoopDesignAndControl | DAC 1 | Loop 1 | minimum_flow_fraction
JSON_PATH:fluid_loops[0]:child_loops[0]:id: | JSON_PATH:fluid_loops[0]:child_loops[0]:id: | JSON_PATH:fluid_loops[0] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 1 | id | [27 empty] | Secondary CHW Loop 1 | [9 empty] | Secondary CHW Loop 1
JSON_PATH:fluid_loops[0]:child_loops[0]:type: | JSON_PATH:fluid_loops[0]:child_loops[0]:type: | JSON_PATH:fluid_loops[0] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 1 | type | [27 empty] | COOLING | [9 empty] | COOLING
JSON_PATH:fluid_loops[1]:id:: | JSON_PATH:fluid_loops[1]:id:: | JSON_PATH:fluid_loops[1] | id |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | id |  |  |  | Purchased CHW 1 |  | Purchased CHW Loop 1 |  |  |  |  | Purchased HW Loop 1 | [5 empty] | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | [5 empty] | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1 | Chiller Loop 1 | Chilled Water Loop 1
JSON_PATH:fluid_loops[1]:type:: | JSON_PATH:fluid_loops[1]:type:: | JSON_PATH:fluid_loops[1] | type |  |  | FluidLoop | Loop 2 | ASHRAE229 1 | type |  |  |  | COOLING |  | COOLING |  |  |  |  | HEATING | [5 empty] | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | [5 empty] | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING | COOLING
JSON_PATH:fluid_loops[1]:child_loops[0]:id: | JSON_PATH:fluid_loops[1]:child_loops[0]:id: | JSON_PATH:fluid_loops[1] | child_loops[0] | id |  | FluidLoop | SecondaryLoop 1 | Loop 2 | id | [16 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 | [6 empty] | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1 |  | Secondary CHW Loop 1
JSON_PATH:fluid_loops[1]:child_loops[0]:type: | JSON_PATH:fluid_loops[1]:child_loops[0]:type: | JSON_PATH:fluid_loops[1] | child_loops[0] | type |  | FluidLoop | SecondaryLoop 1 | Loop 2 | type | [16 empty] | COOLING |  | COOLING |  | COOLING |  | COOLING | [6 empty] | COOLING |  | COOLING |  | COOLING |  | COOLING
VALUES FOR THIS SECTION ONLY
| JSON_PATH:boilers[0]:draft_type:: | JSON_PATH:boilers[0] | draft_type
| JSON_PATH:boilers[0]:rated_capacity:: | JSON_PATH:boilers[0] | rated_capacity
| JSON_PATH:boilers[0]:efficiency:: | JSON_PATH:boilers[0] | efficiency
| JSON_PATH:boilers[0]:efficiency_metric:: | JSON_PATH:boilers[0] | efficiency_metric
| JSON_PATH:boilers[0]:operation_lower_limit:: | JSON_PATH:boilers[0] | operation_lower_limit
| JSON_PATH:boilers[0]:operation_upper_limit:: | JSON_PATH:boilers[0] | operation_upper_limit
| JSON_PATH:boilers[1]:id:: | JSON_PATH:boilers[1] | id
| JSON_PATH:boilers[1]:loop:: | JSON_PATH:boilers[1] | loop
| JSON_PATH:boilers[1]:draft_type:: | JSON_PATH:boilers[1] | draft_type
| JSON_PATH:boilers[1]:design_capacity:: | JSON_PATH:boilers[1] | design_capacity
| JSON_PATH:boilers[1]:energy_source_type:: | JSON_PATH:boilers[1] | energy_source_type
| JSON_PATH:boilers[1]:operation_lower_limit:: | JSON_PATH:boilers[1] | operation_lower_limit
| JSON_PATH:boilers[1]:operation_upper_limit:: | JSON_PATH:boilers[1] | operation_upper_limit
| JSON_PATH:boilers[2]:id:: | JSON_PATH:boilers[2] | id
| JSON_PATH:boilers[2]:loop:: | JSON_PATH:boilers[2] | loop
| JSON_PATH:boilers[2]:design_capacity:: | JSON_PATH:boilers[2] | design_capacity
| JSON_PATH:fluid_loops[0]:child_loops[0]:: | JSON_PATH:fluid_loops[0] | child_loops[0]
| JSON_PATH:fluid_loops[0]:pump_power_per_flow_rate:: | JSON_PATH:fluid_loops[0] | pump_power_per_flow_rate
| JSON_PATH:fluid_loops[0]:heating_design_and_control:id: | JSON_PATH:fluid_loops[0] | heating_design_and_control | id
| JSON_PATH:fluid_loops[0]:heating_design_and_control:is_sized_using_coincident_load: | JSON_PATH:fluid_loops[0] | heating_design_and_control | is_sized_using_coincident_load
| JSON_PATH:fluid_loops[0]:heating_design_and_control:temperature_reset_type: | JSON_PATH:fluid_loops[0] | heating_design_and_control | temperature_reset_type
| JSON_PATH:fluid_loops[0]:heating_design_and_control:design_supply_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_supply_temperature
| JSON_PATH:fluid_loops[0]:heating_design_and_control:design_return_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | design_return_temperature
| JSON_PATH:fluid_loops[0]:heating_design_and_control:outdoor_high_for_loop_supply_reset_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_high_for_loop_supply_reset_temperature
| JSON_PATH:fluid_loops[0]:heating_design_and_control:outdoor_low_for_loop_supply_reset_temperature: | JSON_PATH:fluid_loops[0] | heating_design_and_control | outdoor_low_for_loop_supply_reset_temperature
| JSON_PATH:fluid_loops[0]:heating_design_and_control:minimum_flow_fraction: | JSON_PATH:fluid_loops[0] | heating_design_and_control | minimum_flow_fraction
| JSON_PATH:fluid_loops[0]:heating_design_and_control:flow_control: | JSON_PATH:fluid_loops[0] | heating_design_and_control | flow_control
| JSON_PATH:fluid_loops[0]:heating_design_and_control:operation: | JSON_PATH:fluid_loops[0] | heating_design_and_control | operation
| JSON_PATH:fluid_loops[1]:child_loops[0]:id: | JSON_PATH:fluid_loops[1] | child_loops[0] | id
| JSON_PATH:fluid_loops[1]:child_loops[0]:type: | JSON_PATH:fluid_loops[1] | child_loops[0] | type
| weather:climate zone:: | weather | climate zone

## HVAC_TCDs (hidden)
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | System_1_PTAC | System_3_PSZ_AC | System_7_VAV_HW_Reheat
Section | [10 empty] | 99 | 99 | 99
Rule | [10 empty] | 1 | 2 | 3
Test | [10 empty] | a | a | a
Notes
test_description | [10 empty] | dummy | dummy | dummy
expected_rule_outcome | [10 empty] | pass | pass | pass
template_lookup | [10 empty] | System_1_PTAC | System_3_PSZ_AC | System_7_VAV_HW_Reheat
rmr_template | user | [9 empty] | true | true | true
rmr_template | proposed
rmr_template | baseline
rmr_template | json_template | id |  |  | ASHRAE229 | ASHRAE229 1 | - | id |  |  | ASHRAE229 1 | #N/A | ASHRAE229 1
rmr_template | json_template | weather | climate_zone |  | Calendar | N/A | ASHRAE229 1 | is_leap_year |  |  |  | #N/A
rmr_template | json_template | ruleset_model_instances[0] | id |  | RulesetModelInstance | RMR 1 | ASHRAE229 1 | id |  |  | RMD 1 | #N/A | RMD 1
rmr_template | json_template | JSON_PATH:buildings[0] | id |  | Building | Building 1 | ASHRAE229 1 | id |  |  | Building 1 | #N/A | Building 1
rmr_template | json_template | JSON_PATH:buildings[0] | building_open_schedule |  | Building | Building 1 | ASHRAE229 1 | building_open_schedule |  |  | Required Building Schedule 1 | #N/A | Required Building Schedule 1
rmr_template | json_template | JSON_PATH: building_segments[0] | id |  | BuildingSegment | Building Segment 1 | Building 1 | id |  |  | Building Segment 1 | #N/A | Building Segment 1
rmr_template | json_template | JSON_PATH:zones[0] | id |  | Zone | Zone 1 | Building Segment 1 | id |  |  | Thermal Zone 1 | #N/A | Thermal Zone 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_cooling_setpoint_schedule |  | Zone | Zone 1 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  | Required Cooling Schedule 1 | #N/A | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | thermostat_heating_setpoint_schedule |  | Zone | Zone 1 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  | Required Heating Schedule 1 | #N/A | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | id | Space | Space 1 | Zone 1 | id |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | occupant_multiplier_schedule | Space | Space 1 | Zone 1 | occupant_multiplier_schedule |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | spaces[0] | floor_area | Space | Space 1 | Zone 1 | floor_area | area | ft2 |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | id | Air Terminal | Terminal 1 | Zone 1 | id |  |  | PTAC Terminal 1 | #N/A | VAV Air Terminal 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | is_supply_ducted | Air Terminal | Terminal 1 | Zone 1 | is_supply_ducted |  |  | FALSE | #N/A | true
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_source | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  |  | #N/A | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | heating_from_loop | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  |  | #N/A | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | type | Air Terminal | Terminal 1 | Zone 1 | type |  |  | CONSTANT_AIR_VOLUME | #N/A | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | Air Terminal | Terminal 1 | Zone 1 | served_by_heating_ventilating_air_conditioning_system |  |  | PTAC 1 | #N/A | System 7
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_source | Air Terminal | Terminal 1 | Zone 1 | heating_source |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | cooling_from_loop | Air Terminal | Terminal 1 | Zone 1 | heating_from_loop |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan | Fan | Fan 1 | Terminal 1 | id |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[0] | terminals[0] | fan_configuration | Air Terminal | Terminal 1 | Zone 1 | fan_configuration |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | id |  | Zone | Zone 2 | Building Segment 1 | id |  |  |  | #N/A | Thermal Zone 2
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_cooling_setpoint_schedule |  | Zone | Zone 2 | Building Segment 1 | thermostat_cooling_setpoint_schedule |  |  |  | #N/A | Required Cooling Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | thermostat_heating_setpoint_schedule |  | Zone | Zone 2 | Building Segment 1 | thermostat_heating_setpoint_schedule |  |  |  | #N/A | Required Heating Schedule 1
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | id | Space | Space 2 | Zone 2 | id |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | occupant_multiplier_schedule | Space | Space 2 | Zone 2 | occupant_multiplier_schedule |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | spaces[0] | floor_area | Space | Space 2 | Zone 2 | floor_area | area | ft2 |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | id | Air Terminal | Terminal 2 | Zone 2 | id |  |  |  | #N/A | VAV Air Terminal 2
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | is_supply_ducted | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  |  | #N/A | true
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  |  | #N/A | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | type | Air Terminal | Terminal 2 | Zone 2 | type |  |  |  | #N/A | VARIABLE_AIR_VOLUME
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | served_by_heating_ventilating_air_conditioning_system | Air Terminal | Terminal 2 | Zone 2 | served_by_heating_ventilating_air_conditioning_system |  |  |  | #N/A | System 7
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_source | Air Terminal | Terminal 2 | Zone 2 | heating_source |  |  |  | #N/A | HOT_WATER
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | heating_from_loop | Air Terminal | Terminal 2 | Zone 2 | heating_from_loop |  |  |  | #N/A | Boiler Loop 1
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan | Fan | Fan 2 | Terminal 2 | id |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:zones[1] | terminals[0] | fan_configuration | Air Terminal | Terminal 2 | Zone 2 | fan_configuration |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:heating_ventilating_air_conditioning_systems[0] | id |  | HVAC | HVAC 1 | Building Segment 1 | id |  |  | PTAC 1 | #N/A | System 7
rmr_template | json_template | JSON_PATH:heating_system | id |  | HeatingSystem | Heating System 1 | HVAC 1 | id |  |  | HHW Coil 1 | #N/A
rmr_template | json_template | JSON_PATH:heating_system | heating_system_type |  | HeatingSystem | Heating System 1 | HVAC 1 | heating_system_type |  |  | FLUID_LOOP | #N/A
rmr_template | json_template | JSON_PATH:heating_system | energy_source_type |  | HeatingSystem | Heating System 1 | HVAC 1 | energy_source_type |  |  |  | #N/A
rmr_template | json_template | JSON_PATH:heating_system | hot_water_loop |  | HeatingSystem | Heating System 1 | HVAC 1 | hot_water_loop |  |  | Boiler Loop 1 | #N/A
rmr_template | json_template | JSON_PATH:preheat_system | id |  | HeatingSystem | Heating System 2 | HVAC 1 | id |  |  |  | #N/A | Preheat Coil 1
rmr_template | json_template | JSON_PATH:preheat_system | heating_system_type |  | HeatingSystem | Heating System 2 | HVAC 1 | heating_system_type |  |  |  | #N/A | FLUID_LOOP
rmr_template | json_template | JSON_PATH:preheat_system | hot_water_loop |  | HeatingSystem | Heating System 2 | HVAC 1 | hot_water_loop |  |  |  | #N/A | Boiler Loop 1
rmr_template | json_template | JSON_PATH:fan_system | id |  | Fan System | Fan System 1 | HVAC 1 | id |  |  | CAV Fan System 1 | #N/A | VAV Fan System 1
rmr_template | json_template | JSON_PATH:fan_system | fan_control |  | Fan System | Fan System 1 | HVAC 1 | fan_control |  |  | CONSTANT | #N/A | VARIABLE_SPEED_DRIVE
rmr_template | json_template | JSON_PATH:fan_system | supply_fans[0] | id | Fan | Supply Fan 1 | HVAC 1 | id |  |  | Supply Fan 1 | #N/A | Supply Fan 1
rmr_template | json_template | JSON_PATH:fan_system | return_fans[0] | id | Fan | Return Fan 1 | HVAC 1 | id |  |  |  | #N/A | Return Fan 1
rmr_template | json_template | JSON_PATH:boilers[0] | id |  | Boiler | Boiler 1 | ASHRAE229 1 | id |  |  | Boiler 1 | #N/A | Boiler 1
rmr_template | json_template | JSON_PATH:boilers[0] | loop |  | Boiler | Boiler 1 | ASHRAE229 1 | loop |  |  | Boiler Loop 1 | #N/A | Boiler Loop 1
|  | JSON_PATH:boilers[0] | draft_type |  | Boiler | Boiler 1 | ASHRAE229 1 | draft_type |  |  |  | #N/A
|  | JSON_PATH:boilers[0] | rated_capacity |  | Boiler | Boiler 1 | ASHRAE229 1 | rated_capacity | capacity | Btu/hr |  | #N/A
|  | JSON_PATH:boilers[0] | efficiency |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency |  |  |  | #N/A
|  |  | efficiency_metric |  | Boiler | Boiler 1 | ASHRAE229 1 | efficiency_metric |  |  |  | #N/A
rmr_transformations | user | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | proposed | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | baseline | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2

## Lighting_TCDs (hidden)
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | Lighting Example
Section | [10 empty] | 99
Rule | [10 empty] | 1
Test | [10 empty] | a
Notes
test_description | [10 empty] | dummy
expected_rule_outcome | [10 empty] | pass
template_lookup | [10 empty] | Lighting Example
rmr_template | user | [9 empty] | true
rmr_template | proposed
rmr_template | baseline
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[9 empty] | #REF! | #REF!
rmr_transformations | user | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | proposed | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | baseline | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2

## Envelope_TCDs (hidden)
key1 | key2 | key3 | key4 | key5 | data_group | object_id | parent_id | data_element | unit_type | units | Envelope_Example
Section | [10 empty] | 99
Rule | [10 empty] | 1
Test | [10 empty] | a
Notes
test_description | [10 empty] | dummy
expected_rule_outcome | [10 empty] | pass
template_lookup | [10 empty] | Envelope_Example
rmr_template | user | [9 empty] | true
rmr_template | proposed
rmr_template | baseline
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_template | json_template | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
rmr_transformations | user | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | proposed | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2
rmr_transformations | baseline | JSON_PATH: spaces[0] | interior_lighting[0] | power_per_area |  |  |  |  | power_density | W/ft2

## TCD_old (hidden)
appendix_g_section_id | rule_id | test_id | case_number | rule_description | test_outcome | user_rmr_xpath | test_type | target_rmr | test_target | target_id | target_value
15 | 1 | a | 1 | Number of transformers modeled in User RMR and Baseline RMR are the same | pass | building/transformers/.. | num_of_elements_equal_to | baseline | rmr | triplet_101 | building/transformers/..
15 | 1 | b | 1 | Number of transformers modeled in User RMR and Baseline RMR are the same | fail | building/transformers/.. | num_of_elements_equal_to | baseline | rmr | triplet_102 | building/transformers/..
15 | 6 | a | 1 | Transformer efficiency reported in User RMR equals Table 8.4.4 | pass | building/transformer/transformer/type | value_equal_to | user | self | triplet_101 | Drytype
15 | 6 | a | 2 | Transformer efficiency reported in User RMR equals Table 8.4.4 | pass | building/transformer/transformer/phase | value_equal_to | user | table | table_8.4.4 | transformer_efficiency